## Boiler
Template Category | Boilers - Gas/Oil
Template Version | v1
Category Description | Gas & Oil Fired Boilers used for space heating and indirect hot water generation
Classification System
Classification | Value
Suitability for Use | Approved
Template Custodian | CIBSE
Information Category | Parameter Name | Value | Units | Notes
Manufacturer Data
Specifications | Manufacturer | Bosch Thermotechnology | Text
Specifications | Manufacturer Website | www.buderus.co.uk | URL
Specifications | Product Range | Condens 7000 F (RH) | Text
Specifications | Product Model Number | 250kW | Text | Or Code
Specifications | CE Approval | CE – 0085CS0098 | Text | Number, Yes, No
Specifications | Product Literature | www.bosch-thermotechnology.com/gb/en/commercial-industrial/home/ | URL
Specifications | Features | Gas Condensing Boiler | Text | Free text to describe product
Construction Data
Specifications | Type | Space heating | Text
Specifications | Configuration | Single boiler | Enumeration
Specifications | Shape | Rectangular (Vertical) | Enumeration
Specifications | External Material | Steel | Enumeration
Specifications | Colour | Anthracite RAL 7016 | Text | e.g. RAL, Colour
Specifications | Finish | Paint | Text | e.g. Anodised, Brushed, Painted, Natural (Self-finish)
Specifications | Mounting | Floor Standing | Enumeration
Specifications | Control Options | Modulating | Enumeration
Specifications | Burner Configuration | Integral | Enumeration | State whether burner is integral or separate
Specifications | Heat Exchanger Material | Aluminium | Enumeration
Specifications | Fuel Connection Type | Threaded | Enumeration
Specifications | Flow and Return Connection Type | Flanged | Enumeration
Specifications | Drain Connection Type | Plain | Enumeration
Specifications | Safety Valve Connection Type | Threaded | Enumeration
Specifications | Condensate Drain Type | Plain | Enumeration
Specifications | Flue or Air Intake Classification | B23, C13, C33, C53, C63, C83, C93 | Text | Flue/air intake classification standard, e.g. 'B23'
Application Data
Specifications | Reference Standard | BS EN | Text | BS, EN, ISO
Dimensional Data
Specifications | Overall Length | 1317 | mm | Depth or Diameter
Specifications | Overall Width | 670 | mm
Specifications | Overall Height | 1710 | mm
Specifications | Gross Weight | 196.8 | kg | Depth or Diameter
Specifications | Water Content | 38.8 | litres
Specifications | Shipping Weight | 158 | kg | Equates to dry weight of unit plus packaging allowance
Specifications | Access Clearance Top | 0 | mm | Access required for maintenance of this item
Specifications | Access Clearance Bottom | 0 | mm | Access required for maintenance of this item
Specifications | Access Clearance Left | 100 | mm | Access required for maintenance of this item
Specifications | Access Clearance Right | 600 | mm | Access required for maintenance of this item
Specifications | Access Clearance Front | 800 | mm | Access required for maintenance of this item
Specifications | Access Clearance Rear | 150 | mm | Access required for maintenance of this item
Specifications | Fuel Connection Size | R 11/4" | inches | Choose units from dropdown
Specifications | Flow and Return Connection Size | DN65 | mm | Choose units from dropdown
Specifications | Drain Connection Size | 15 | mm | Choose units from dropdown
Specifications | Safety Valve Connection Size | R 11/4" | inches | Choose units from dropdown
Specifications | Condensate Drain Size | R 3/4" | inches | Choose units from dropdown
Specifications | Flue Connection Size | 200 | mm | Also state whether internal or external in notes
Specifications | Air Inlet Connection Size | 160 | mm | Also state whether internal or external in notes
Performance Data
Specifications | Sound Pressure Level | 58 | dBA | Measured at 1m from the casing
Specifications | Primary Fuel | Gas - NG | Enumeration
Specifications | Secondary Fuel | No Secondary Fuel | Enumeration | If Not Applicable, choose 'No Secondary Fuel'
Specifications | Gas Consumption rate | 25.2 | m3/h | If Not Applicable Mark '0'
Specifications | Oil Consumption rate |  | l/h | If Not Applicable Mark '0'
Specifications | Rated Output | 250 | kW | Product rated output
Specifications | Rated Criteria | 50/30 | Enumeration | Flow and Return differential
Specifications | Rated Efficiency at Full Load | 105.1 | % | Rated Efficiency at 100% Load
Specifications | Rated Efficiency at Part Load | 108.4 | % | Rated Efficiency at 30% Load
Specifications | Seasonal Efficiency | 97.1 | % | Refer to Building Regulations
Specifications | Turndown Ratio | 1:6 | Text | Ratio of maximum to minimum fire
Specifications | Emissions | 36 | mg/kWh | NOx Emissions at 0% O2
Specifications | Maximum Operating Pressure | 6 | bar | Water side
Specifications | Minimum Operating Pressure | 1 | bar | Water side
Specifications | Nominal Gas Inlet Pressure | 20 | mbar | Standard gas inlet pressure
Specifications | Minimum Gas Inlet Pressure | 17 | mbar | Minimum safe gas inlet pressure
Specifications | Maximum Gas Inlet Pressure | 25 | mbar | Maximum safe gas inlet pressure
Specifications | Nominal Oil Inlet Pressure |  | mbar | Standard oil inlet pressure
Specifications | Minimum Oil Inlet Pressure |  | mbar | Minimum safe oil inlet pressure
Specifications | Maximum Oil Inlet Pressure |  | mbar | Maximum safe oil inlet pressure
Electrical Data
Specifications | Voltage | 230 | Volts
Specifications | Supply Phase | 1 | Number | 1,3
Specifications | Frequency | 50 | Hertz | eg. N/A, DC, 50,60, Other, UserDefined
Specifications | IP Rating | IPX 0D | Text | Ingress Protection rating e.g. IP56
Specifications | IK Rating |  | Text | Impact Resistance rating
Specifications | Starting Current |  | Amps
Specifications | Full Load Current |  | Amps
Specifications | Fuse Rating | 10 | Amps | At UK standard voltage
Specifications | Maximum Power Consumption | 298 | W
Specifications | Minimum Power Consumption | 41 | W
Controls
Specifications | Type | External | Enumeration | State whether controls are internal or external
Specifications | BMS Links | Y | Y/N
Specifications | Interlocks | Y | Y/N
Sustainability
Sustainable Material BREEAM etc | Embodied Carbon |  | kgCO2e | University of Bath ICE Data if none other available (Awaiting industry standard)
Sustainable Material BREEAM etc | Life Cycle Analysis |  | Number | BREEAM (Awaiting industry standard)
Sustainable Material BREEAM etc | Location of Manufacturer |  | GridRef | Northing, Easting (Awaiting industry standard)
Sustainable Material BREEAM etc | Green Guide for Specification |  | Enumeration | A - E (Awaiting industry standard)
Sustainable Material BREEAM etc | Environmental Product Declaration |  | Text | 3rd Party Verification (Awaiting industry standard)
Sustainable Material BREEAM etc | Responsible Sourcing of Materials |  | Enumeration | Endorsing body (Awaiting industry standard)
Sustainable Material ETL | Energy Technology List |  | URL | Hyperlink to ETL webpage for product. If Not Applicable Mark '0'
Sustainable Material LEED v.4 | Responsible Extraction of Materials |  | Text | (Awaiting industry standard)
Sustainable Material LEED v.4 | Material Ingredient Reporting |  | Text | (Awaiting industry standard)
Sustainable Product Directive Ecodesign | ErP Energy Label | N | Y/N
Operations & Maintenance
Facilities/Asset Management | O&M Manual | www.bosch-thermotechnology.com/gb/en/commercial-industrial/home/ | URL | Hyperlink to Manufacturer O&M Data
Facilities/Asset Management | Daily | No | Text | Maintenance tasks or SFG20 codes. If Not Applicable Mark '0'
Facilities/Asset Management | Weekly | System pressure check | Text | Maintenance tasks or SFG20 codes. If Not Applicable Mark '0'
Facilities/Asset Management | Monthly | No | Text | Maintenance tasks or SFG20 codes. If Not Applicable Mark '0'
Facilities/Asset Management | Quarterly | No | Text | Maintenance tasks or SFG20 codes. If Not Applicable Mark '0'
Facilities/Asset Management | 6 Monthly | No | Text | Maintenance tasks or SFG20 codes. If Not Applicable Mark '0'
Facilities/Asset Management | Annually | Annual service | Text | Maintenance tasks or SFG20 codes. If Not Applicable Mark '0'
Facilities/Asset Management | Bespoke Timeframe | No | Text | Maintenance tasks or SFG20 codes. If Not Applicable Mark '0'
Facilities/Asset Management | Maintenance Required 0-300hrs | No | Text | Maintenance tasks required during this time frame. If Not Applicable Mark '0'
Facilities/Asset Management | Maintenance Required 301-600hrs | No | Text | Maintenance tasks required during this time frame. If Not Applicable Mark '0'
Facilities/Asset Management | Maintenance Required 601-1000hrs | No | Text | Maintenance tasks required during this time frame. If Not Applicable Mark '0'
Facilities/Asset Management | Maintenance Required 1001-2000hrs | No | Text | Maintenance tasks required during this time frame. If Not Applicable Mark '0'
Facilities/Asset Management | Maintenance Required 2001-4000hrs | No | Text | Maintenance tasks required during this time frame. If Not Applicable Mark '0'
Facilities/Asset Management | Maintenance Required 40001-8000hrs | No | Text | Maintenance tasks required during this time frame. If Not Applicable Mark '0'
Facilities/Asset Management | Maintenance Required 8001-12000hrs | No | Text | Maintenance tasks required during this time frame. If Not Applicable Mark '0'
Facilities/Asset Management | Expected Life | 15-20 | Years
Facilities/Asset Management | Warranty ID | Serial number and end user registration | Text
This spreadsheet is the property of CIBSE although it can be freely used in the ways described, and completed with data specific to particular products. It is important that the Categories and Parameters given on the form are not changed. It is also important that where units of measurement are defined on the form that these too are followed. Any comment or suggestion on their revision should be addressed to pdt@cibse.org