## General
General Information
The ACC-MT provides a Modbus/TCP interface on the dedicated LAN2 port (located on the accessory AC-EXP). This interface provides the data points described in this document for each “XYE Connection” on dedicated IP addresses. Those can be on the same subnet but must be on a different subnet as the LAN1 interface, best on a physically separate BMS net-work, as the Modbus/TCP interface does not implement any sort of user authentication. The Modbus/TCP datagram requires a “Modbus TCP Server Address”. This can be either ‘1’ or ‘255’.

## Discret Inputs
Discrete Inputs (Read Only)
Indoor Unit
Discrete Input | Function Code | Register Address | Data Length | Description | Available since
Indoor unit 0 | 2 | 0 | 1bit | 0: Off, 1: On | AF5300, AF6300: 2.2.0 AF4300: 2.3.0 AF5301: 3.0.0
| 2 | 1 | 1bit | 0: No error, 1: Error
| 2 | 2 | 1bit | 0: Offline, 1: Online
| 2 | 3 | 1bit | Reserved
| 2 | 4 | 1bit | Reserved
| 2 | 5 | 1bit | Reserved
| 2 | 6 | 1bit | Reserved
| 2 | 7 | 1bit | Reserved
Indoor unit N (N=0...63) | 2 | N * 8 + 0 | 1bit | 0: Off, 1: On | AF5300, AF6300: 2.2.0 AF4300: 2.3.0 AF5301: 3.0.0
| 2 | N * 8 + 1 | 1bit | 0: No error, 1: Error
| 2 | N * 8 + 2 | 1bit | 0: Offline, 1: Online
| 2 | N * 8 + 3 | 1bit | Reserved
| 2 | N * 8 + 4 | 1bit | Reserved
| 2 | N * 8 + 5 | 1bit | Reserved
| 2 | N * 8 + 6 | 1bit | Reserved
| 2 | N * 8 + 7 | 1bit | Reserved
Outdoor Unit
Discrete Input | Function Code | Register Address | Data Length | Description | Available since
Outdoor unit 0 | 2 | 1000 | 1bit | 0: Off, 1: On | AF5300, AF6300: 2.2.0 AF4300: 2.3.0 AF5301: 3.0.0
| 2 | 1001 | 1bit | 0: No error, 1: Error
| 2 | 1002 | 1bit | 0: Offline, 1: Online
| 2 | 1003 | 1bit | Reserved
| 2 | 1004 | 1bit | Reserved
| 2 | 1005 | 1bit | Reserved
| 2 | 1006 | 1bit | Reserved
| 2 | 1007 | 1bit | Reserved
Outdoor unit N (N=0...31) | 2 | N * 8 + 1000 | 1bit | 0: Off, 1: On | AF5300, AF6300: 2.2.0 AF4300: 2.3.0 AF5301: 3.0.0
| 2 | N * 8 + 1001 | 1bit | 0: No error, 1: Error
| 2 | N * 8 + 1002 | 1bit | 0: Offline, 1: Online
| 2 | N * 8 + 1003 | 1bit | Reserved
| 2 | N * 8 + 1004 | 1bit | Reserved
| 2 | N * 8 + 1005 | 1bit | Reserved
| 2 | N * 8 + 1006 | 1bit | Reserved
| 2 | N * 8 + 1007 | 1bit | Reserved

## Input Registers
Input Registers (Read Only)
Indoor Unit
Input Register | Function Code | Register Address | Data Length | Variable Name | Description | Available since
Indoor unit 0 | 4 | 0 | 2 bytes | Mode | Regular indoor unit mode: 1: Fan, 2: Cool, 3: Heat, 6: Dry, 16: Auto ERV mode: 1: Free cool, 2: Heat exchange, 3: Bypass, 16: Auto | AF5300, AF6300: 2.2.0 AF4300: 2.3.0 AF5301: 3.0.0
| 4 | 1 | 2 bytes | Fan speed | Seven fan speeds: 1-7: fan speed 1...7 Three fan speeds: 1: Low speed, 3: Medium speed, 7: High speed Auto fan speed: 255
| 4 | 2 | 2 bytes | Temperature setting For AF6300 only: Dual Setpoint cooling temperature in auto mode | Actual temperature ( °C) × 10
| 4 | 3 | 2 bytes | For AF6300 only: Dual Setpoint heating temperature in auto mode | Actual temperature ( °C) × 10 | AF6300: 2.2.0
| 4 | 4 | 2 bytes | Indoor temperature | Actual temperature ( °C) × 10 | AF5300, AF6300: 2.2.0 AF4300: 2.3.0 AF5301: 3.0.0
| 4 | 5 | 2 bytes | Error code
| 4 | 6 | 2 bytes | Idu Type
| 4 | 7 | 2 bytes | Remote controller lock | 0: Unlock, 1: Lock | AF5300, AF6300: 2.2.0 AF4300, AF5301: 3.0.0
| 4 | 8 | 2 bytes | Wired controller lock | 0: Unlock, 1: Lock
| 4 | 9 | 2 bytes | Vertical Swing | Vertical swing angle setting: 0: Setting not available 1-5: Vertical swing angle 255: Auto vertical swing | AF5300, AF6300, AF4300, AF5301: 3.0.0
| 4 | 10 | 2 bytes | For AF4300, AF5301 only: Vertical Swing 1 | Vertical swing angle setting: 0: Setting not available 1-5: Vertical swing angle 255: Auto vertical swing | AF4300, AF5301: 3.0.0
| 4 | 11 | 2 bytes | For AF4300, AF5301 only: Vertical Swing 2 | Vertical swing angle setting: 0: Setting not available 1-5: Vertical swing angle 255: Auto vertical swing | AF4300, AF5301: 3.0.0
| 4 | 12 | 2 bytes | For AF4300, AF5301 only: Vertical Swing 3 | Vertical swing angle setting: 0: Setting not available 1-5: Vertical swing angle 255: Auto vertical swing | AF4300, AF5301: 3.0.0
| 4 | 13 | 2 bytes | For AF4300, AF5301 only: Vertical Swing 4 | Vertical swing angle setting: 0: Setting not available 1-5: Vertical swing angle 255: Auto vertical swing | AF4300, AF5301: 3.0.0
| 4 | 14 | 2 bytes | Reserved
| 4 | 15 | 2 bytes | Reserved
| 4 | 16 | 2 bytes | Reserved
| 4 | 17 | 2 bytes | Reserved
| 4 | 18 | 2 bytes | Reserved
| 4 | 19 | 2 bytes | Reserved
| 4 | 20 | 2 bytes | Reserved
| 4 | 21 | 2 bytes | Reserved
|  | 22 | 2 bytes | Reserved
| 4 | 23 | 2 bytes | Reserved
Indoor unit N (N=0...63) | 4 | N * 24 + 0 | 2 bytes | Mode | Regular indoor unit mode: 1: Fan, 2: Cool, 3: Heat, 6: Dry, 16: Auto ERV mode: 1: Free cool, 2: Heat exchange, 3: Bypass, 16: Auto | AF5300, AF6300: 2.2.0 AF4300: 2.3.0 AF5301: 3.0.0
| 4 | N * 24 + 1 | 2 bytes | Fan speed | Seven fan speeds: 1-7: fan speed 1...7 Three fan speeds: 1: Low speed, 3: Medium speed, 7: High speed Auto fan speed: 255
| 4 | N * 24 + 2 | 2 bytes | Temperature setting For AF6300 only: Dual Setpoint cooling temperature in auto mode | Actual temperature ( °C) × 10
| 4 | N * 24 + 3 | 2 bytes | For AF6300 only: Dual Setpoint heating temperature in auto mode | Actual temperature ( °C) × 10 | AF6300: 2.2.0
| 4 | N * 24 + 4 | 2 bytes | Indoor temperature | Actual temperature ( °C) × 10 | AF5300, AF6300: 2.2.0 AF4300: 2.3.0 AF5301: 3.0.0
| 4 | N * 24 + 5 | 2 bytes | Error code
| 4 | N * 24 + 6 | 2 bytes | Idu Type
| 4 | N * 24 + 7 | 2 bytes | Remote controller lock | 0: Unlock, 1: Lock | AF5300, AF6300: 2.2.0 AF4300, AF5301: 3.0.0
| 4 | N * 24 + 8 | 2 bytes | Wired controller lock | 0: Unlock, 1: Lock
| 4 | N * 24 + 9 | 2 bytes | Vertical Swing | Vertical swing angle setting: 0: Setting not available 1-5: Vertical swing angle 255: Auto vertical swing | AF5300, AF6300, AF4300, AF5301: 3.0.0
| 4 | N * 24 + 10 | 2 bytes | For AF4300, AF5301 only: Vertical Swing 1 | Vertical swing angle setting: 0: Setting not available 1-5: Vertical swing angle 255: Auto vertical swing | AF4300, AF5301: 3.0.0
| 4 | N * 24 + 11 | 2 bytes | For AF4300, AF5301 only: Vertical Swing 2 | Vertical swing angle setting: 0: Setting not available 1-5: Vertical swing angle 255: Auto vertical swing | AF4300, AF5301: 3.0.0
| 4 | N * 24 + 12 | 2 bytes | For AF4300, AF5301 only: Vertical Swing 3 | Vertical swing angle setting: 0: Setting not available 1-5: Vertical swing angle 255: Auto vertical swing | AF4300, AF5301: 3.0.0
| 4 | N * 24 + 13 | 2 bytes | For AF4300, AF5301 only: Vertical Swing 4 | Vertical swing angle setting: 0: Setting not available 1-5: Vertical swing angle 255: Auto vertical swing | AF4300, AF5301: 3.0.0
| 4 | N * 24 + 14 | 2 bytes | Reserved
| 4 | N * 24 + 15 | 2 bytes | Reserved
| 4 | N * 24 + 16 | 2 bytes | Reserved
| 4 | N * 24 + 17 | 2 bytes | Reserved
|  | N * 24 + 18 | 2 bytes | Reserved
| 4 | N * 24 + 19 | 2 bytes | Reserved
| 4 | N * 24 + 20 | 2 bytes | Reserved
| 4 | N * 24 + 21 | 2 bytes | Reserved
| 4 | N * 24 + 22 | 2 bytes | Reserved
| 4 | N * 24 + 23 | 2 bytes | Reserved
Outdoor Unit
Discrete Input | Function Code | Register Address | Data Length | Variable Name | Description | Available since
Outdoor unit 0 | 4 | 2000 | 2 bytes | Operating mode | 0: Off, 1: Cool, 2: Heat, 3: Forced cool, 4: Master cool, 5: Master heat | AF5300, AF6300: 2.2.0 AF4300: 2.3.0 AF5301: 3.0.0
| 4 | 2001 | 2 bytes | Outdoor temperature | Actual temperature ( °C) × 10
| 4 | 2002 | 2 bytes | Number of operating indoor units | It indicates the actual number of indoor units that require power.
| 4 | 2003 | 2 bytes | Error code | Error code
| 4 | 2004 | 2 bytes | Reserved
| 4 | 2005 | 2 bytes | Reserved
| 4 | 2006 | 2 bytes | Reserved
| 4 | 2007 | 2 bytes | Reserved
| 4 | 2008 | 2 bytes | Reserved
| 4 | 2009 | 2 bytes | Reserved
| 4 | 2010 | 2 bytes | Reserved
| 4 | 2011 | 2 bytes | Reserved
| 4 | 2012 | 2 bytes | Reserved
| 4 | 2013 | 2 bytes | Reserved
| 4 | 2014 | 2 bytes | Reserved
| 4 | 2015 | 2 bytes | Reserved
Outdoor unit N (N=0...31) | 4 | N * 16 + 2000 | 2 bytes | Operating mode | 0: Off, 1: Fan, 2: Cooling, 3: Heating, 4: Forced cooling, 5: Master cooling, 6: Master heating | AF5300, AF6300: 2.2.0 AF4300: 2.3.0 AF5301: 3.0.0
| 4 | N * 16 + 2001 | 2 bytes | Outdoor temperature | Actual temperature ( °C) × 10
| 4 | N * 16 + 2002 | 2 bytes | Number of operating indoor units | It indicates the actual number of indoor units that require power.
| 4 | N * 16 + 2003 | 2 bytes | Error code | Error code
| 4 | N * 16 + 2004 | 2 bytes | Reserved
| 4 | N * 16 + 2005 | 2 bytes | Reserved
| 4 | N * 16 + 2006 | 2 bytes | Reserved
| 4 | N * 16 + 2007 | 2 bytes | Reserved
| 4 | N * 16 + 2008 | 2 bytes | Reserved
| 4 | N * 16 + 2009 | 2 bytes | Reserved
| 4 | N * 16 + 2010 | 2 bytes | Reserved
| 4 | N * 16 + 2011 | 2 bytes | Reserved
| 4 | N * 16 + 2012 | 2 bytes | Reserved
| 4 | N * 16 + 2013 | 2 bytes | Reserved
| 4 | N * 16 + 2014 | 2 bytes | Reserved
| 4 | N * 16 + 2015 | 2 bytes | Reserved

## Holding Register
Holding Registers (Write Only) |  |  |  |  | Modbus TCP Server-Address needs to be either 1 or 255
Indoor Unit
Holding Register | Function Code | Register Address | Data Length | Variable Name | Description | Available since
Indoor unit 0 | 16 | 0 | 2bytes | Power on / off | 0: Off, 1: On | AF5300, AF6300: 2.2.0 AF4300: 2.3.0 AF5301: 3.0.0
| 16 | 1 | 2bytes | Mode | VRF unit mode: 1: Fan, 2: Cool, 3: Heat, 6: Dry, 16: Auto ERV mode: 1: Free cool, 2: Heat exchange, 3: Bypass, 16: Auto
| 16 | 2 | 2bytes | Fan speed | Seven fan speeds: 1-7: fan speed 1...7 Three fan speeds: 1: Low speed, 3: Medium speed, 7: High speed Fan Speed Auto: 255
| 16 | 3 | 2bytes | Set temperature For AF6300 only: Dual Setpoint cooling temperature in auto mode | Actual temperature ( °C) × 10
| 16 | 4 | 2bytes | For AF6300 only: Dual Setpoint heating temperature in auto mode | Actual temperature ( °C) × 10 | AF6300: 2.2.0
| 16 | 5 | 2bytes | Remote controller lock | 0: Unlock, 1: Lock | AF5300, AF6300: 2.2.0 AF4300, AF5301: 3.0.0
| 16 | 6 | 2bytes | Wired controller lock | 0: Unlock, 1: Lock
| 16 | 7 | 2bytes | Vertical Swing | Vertical swing angle setting: 1-5: Vertical swing angle 255: Auto vertical swing | AF5300, AF6300, AF4300, AF5301: 3.0.0
| 16 | 8 | 2bytes | For AF4300, AF5301 only: Vertical Swing 1 | Vertical swing angle setting: 1-5: Vertical swing angle 255: Auto vertical swing | AF4300, AF5301: 3.0.0
| 16 | 9 | 2bytes | For AF4300, AF5301 only: Vertical Swing 2 | Vertical swing angle setting: 1-5: Vertical swing angle 255: Auto vertical swing | AF4300, AF5301: 3.0.0
| 16 | 10 | 2bytes | For AF4300, AF5301 only: Vertical Swing 3 | Vertical swing angle setting: 1-5: Vertical swing angle 255: Auto vertical swing | AF4300, AF5301: 3.0.0
| 16 | 11 | 2bytes | For AF4300, AF5301 only: Vertical Swing 4 | Vertical swing angle setting: 1-5: Vertical swing angle 255: Auto vertical swing | AF4300, AF5301: 3.0.0
| 16 | 12 | 2bytes | Reserved
| 16 | 13 | 2bytes | Reserved
| 16 | 14 | 2bytes | Reserved
| 16 | 15 | 2bytes | Reserved
| 16 | 16 | 2bytes | Reserved
| 16 | 17 | 2bytes | Reserved
| 16 | 18 | 2bytes | Reserved
| 16 | 19 | 2bytes | Reserved
| 16 | 20 | 2bytes | Reserved
| 16 | 21 | 2bytes | Reserved
| 16 | 22 | 2bytes | Reserved
| 16 | 23 | 2bytes | Reserved
Indoor unit N (N=0...63) | 16 | N * 24 + 0 | 2bytes | Power on / off | 0: Off, 1: On | AF5300, AF6300: 2.2.0 AF4300: 2.3.0 AF5301: 3.0.0
| 16 | N * 24 + 1 | 2bytes | Mode | VRF unit mode: 1: Fan, 2: Cool, 3: Heat, 6: Dry, 16: Auto ERV mode: 1: Free cool, 2: Heat exchange, 3: Bypass, 16: Auto
| 16 | N * 24 + 2 | 2bytes | Fan speed | Seven fan speeds: 1-7: fan speed 1...7 Three fan speeds: 1: Low speed, 3: Medium speed, 7: High speed Fan Speed Auto: 255
| 16 | N * 24 + 3 | 2bytes | Set temperature/ Dual Setpoint cooling temperature in auto mode Dual Setpoint Temperature is only supported for AF6300 systems | Actual temperature ( °C) × 10
| 16 | N * 24 + 4 | 2bytes | Dual Setpoint heating temperature in auto mode Dual Setpoint Temperature is only supported for AF6300 systems | Actual temperature ( °C) × 10 | AF6300: 2.2.0
| 16 | N * 24 + 5 | 2bytes | Remote controller lock | 0: Unlock, 1: Lock | AF5300, AF6300: 2.2.0 AF4300, AF5301: 3.0.0
| 16 | N * 24 + 6 | 2bytes | Wired controller lock | 0: Unlock, 1: Lock
| 16 | N * 24 + 7 | 2bytes | Vertical Swing | Vertical swing angle setting: 1-5: Vertical swing angle 255: Auto vertical swing | AF5300, AF6300, AF4300, AF5301: 3.0.0
| 16 | N * 24 + 8 | 2bytes | For AF4300, AF5301 only: Vertical Swing 1 | Vertical swing angle setting: 1-5: Vertical swing angle 255: Auto vertical swing | AF4300, AF5301: 3.0.0
| 16 | N * 24 + 9 | 2bytes | For AF4300, AF5301 only: Vertical Swing 2 | Vertical swing angle setting: 1-5: Vertical swing angle 255: Auto vertical swing | AF4300, AF5301: 3.0.0
| 16 | N * 24 + 10 | 2bytes | For AF4300, AF5301 only: Vertical Swing 3 | Vertical swing angle setting: 1-5: Vertical swing angle 255: Auto vertical swing | AF4300, AF5301: 3.0.0
| 16 | N * 24 + 11 | 2bytes | For AF4300, AF5301 only: Vertical Swing 4 | Vertical swing angle setting: 1-5: Vertical swing angle 255: Auto vertical swing | AF4300, AF5301: 3.0.0
| 16 | N * 24 + 12 | 2bytes | Reserved
| 16 | N * 24 + 13 | 2bytes | Reserved
| 16 | N * 24 + 14 | 2bytes | Reserved
| 16 | N * 24 + 15 | 2bytes | Reserved
| 16 | N * 24 + 16 | 2bytes | Reserved
| 16 | N * 24 + 17 | 2bytes | Reserved
| 16 | N * 24 + 18 | 2bytes | Reserved
| 16 | N * 24 + 19 | 2bytes | Reserved
| 16 | N * 24 + 20 | 2bytes | Reserved
| 16 | N * 24 + 21 | 2bytes | Reserved
| 16 | N * 24 + 22 | 2bytes | Reserved
| 16 | N * 24 + 23 | 2bytes | Reserved
All Systems
Holding Register | Function Code | Register Address | Data Length | Variable Name | Description | Available since
All off | 16 | 2000 | 2bytes | 1: All off |  | AF5300, AF6300: 2.2.2 AF4300: 2.3.0 AF5301: 3.0.0
Refrigerant Systems
Holding Register | Function Code | Register Address | Data Length | Variable Name | Description | Available since
Refigerant System 0 | 16 | 3000 | 2bytes | Output Limitiation | 0: 100%, 1: 90%, 2: 80%, 3: 70%, 4: 60%, 5: 50%, 6: 40% | AF5300, AF6300: 2.2.2 AF4300: 2.4.0 AF5301: 3.0.0
| 16 | 3001 | 2bytes | Reserved
| 16 | 3002 | 2bytes | Reserved
| 16 | 3003 | 2bytes | Reserved
| 16 | 3004 | 2bytes | Reserved
| 16 | 3005 | 2bytes | Reserved
| 16 | 3006 | 2bytes | Reserved
| 16 | 3007 | 2bytes | Reserved
Refigerant System N N=0...7 | 16 | N * 8 + 3000 | 2bytes | Output Limitiation | 0: 100%, 1: 90%, 2: 80%, 3: 70%, 4: 60%, 5: 50%, 6: 40% | AF5300, AF6300: 2.2.2 AF4300: 2.4.0 AF5301: 3.0.0
| 16 | N * 8 + 3001 | 2bytes | Reserved
| 16 | N * 8 + 3002 | 2bytes | Reserved
| 16 | N * 8 + 3003 | 2bytes | Reserved
| 16 | N * 8 + 3004 | 2bytes | Reserved
| 16 | N * 8 + 3005 | 2bytes | Reserved
| 16 | N * 8 + 3006 | 2bytes | Reserved
| 16 | N * 8 + 3007 | 2bytes | Reserved