## Cover
Customer documentation
Modbus TCP/IP data point list for Logamatic 5000/Control 8000 Series
Date |  | 2023-08-11
Company |  | Bosch Thermotechnik GmbH
Product |  | Logamatic 5000 & Control 8000
Product version |  | 2.0
Description
This document contrains all Modbus TCP/IP data points from the Logamatic 5000/Control 8000. You can use this data point list to control the unit via your BAS. Fur further information, please read the usermanual "Hinweise zur Ansteuerung des Regelgeräts Logamatic".
Information about the data point list
You can find on this page the explanation of the used columns of the Modbus TCP/IP datapoint list from the Logamatic 5000/Control 8000.
Excel sheet | The addresses of the datapoints change depending on the usage of the Logamatic 5000/Control 8000 (Master, Slave01, Slave02, ..). Please select the corresponding sheet of integration from your control unit.
Register Type | Contains the register type that should be used (holding or input register).
Read or Write Permissions | Contains the information about whether the register is read only (R) or readable and writable (W).
Modbus Address | Contains the address of the register.
Bitblock Bit | If the information is contained in a bit block, this information indicates the particular bit in the bit block.
Component | Functional component of the data point.
Name | Name of the data point.
Min | Minimum value that can be read or written.
Max | Maximum value that can be read or written.
Range | Meaning of the number range.
Unit | Unit of the data point.
Float to Int Factor | Conversion factor, which must be used to get the correct value. This is necessary to transfer decimal places.

## Master
Register Type | Permissions | Address | Bitblock Bit | Component | Name | Min | Max | Range | Unit | DataType | Float to Int Factor
HOLDING_REGISTER | Write | 0 |  | System | Heartbeat (In) |  |  |  |  | int
HOLDING_REGISTER | Read | 1 |  | System | Heartbeat (Out) |  |  |  |  | int
HOLDING_REGISTER | Write | 7 |  | DomesticHotWater Zm/Ems | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 8 |  | DomesticHotWater Zm/Ems | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 9 |  | DomesticHotWater Zm/Ems | Thermal Disinfection Setpoint | 65 | 75 |  | °C | int | x10
HOLDING_REGISTER | Write | 10 |  | DomesticHotWater Zm | Setpoint Auto Day | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 11 |  | DomesticHotWater Zm | Setpoint Auto Night | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 12 |  | DomesticHotWater Zm | Setpoint Manual Day | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 13 |  | DomesticHotWater Zm | Setpoint Manual Night | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 14 |  | DomesticHotWater Zm | Setpoint Holiday | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 15 |  | DomesticHotWater Zm/Ems | Circulation Pump Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 16 |  | DomesticHotWater Zm/Ems | Circulation Pump Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 17 |  | DomesticHotWater Zm/Ems | Disinfection Frequency | 0 | 7 | 0-Daily 1-Monday 2-Tuesday 3-Wednesday 4-Thursday 5-Friday 6-Saturday 7-Sunday |  | int
HOLDING_REGISTER | Write | 18 |  | DomesticHotWater Zm/Ems | Disinfection Start Hour | 0 | 23 |  | h | int
HOLDING_REGISTER | Write | 21 |  | DomesticHotWater Fm | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 22 |  | DomesticHotWater Fm | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 23 |  | DomesticHotWater Fm | Thermal Disinfection Setpoint | 65 | 75 |  | °C | int | x10
HOLDING_REGISTER | Write | 24 |  | DomesticHotWater Fm | Setpoint Auto Day | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 25 |  | DomesticHotWater Fm | Setpoint Auto Night | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 26 |  | DomesticHotWater Fm | Setpoint Manual Day | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 27 |  | DomesticHotWater Fm | Setpoint Manual Night | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 28 |  | DomesticHotWater Fm | Setpoint Holiday | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 29 |  | DomesticHotWater Fm | Circulation Pump Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 30 |  | DomesticHotWater Fm | Circulation Pump Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 31 |  | DomesticHotWater Fm | Disinfection Frequency | 0 | 7 | 0-Daily 1-Monday 2-Tuesday 3-Wednesday 4-Thursday 5-Friday 6-Saturday 7-Sunday |  | int
HOLDING_REGISTER | Write | 32 |  | DomesticHotWater Fm | Disinfection Start Hour | 0 | 23 |  | h | int
HOLDING_REGISTER | Read | 39 |  | Boiler | Control Type | 0 | 4 | 0-None 1-Safe 2-Ems 3-7Pole 4-Substation |  | int
HOLDING_REGISTER | Write | 43 |  | AlternativeHeatSource | Operation Mode Request Auto Day | 20 | 99 |  | °C | int
HOLDING_REGISTER | Write | 44 |  | AlternativeHeatSource | Operation Mode Request Auto Night | 20 | 99 |  | °C | int
HOLDING_REGISTER | Write | 45 |  | AlternativeHeatSource | Operation Mode Request Manual Day | 20 | 99 |  | °C | int
HOLDING_REGISTER | Write | 46 |  | AlternativeHeatSource | Operation Mode Request Manual Night | 20 | 99 |  | °C | int
HOLDING_REGISTER | Write | 47 |  | AlternativeHeatSource | Operation Mode Request Holiday | 20 | 99 |  | °C | int
HOLDING_REGISTER | Write | 48 |  | AlternativeHeatSource | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 49 |  | AlternativeHeatSource | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 50 |  | AlternativeHeatSource | Return Control Setpoint User | 10 | 70 |  | °C | int
HOLDING_REGISTER | Write | 57 |  | HydraulicCircuit Zm | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 58 |  | HydraulicCircuit Zm | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 59 |  | HydraulicCircuit Zm | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 60 |  | HydraulicCircuit Zm | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 61 |  | HydraulicCircuit Zm | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 62 |  | HydraulicCircuit Zm | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 63 |  | HydraulicCircuit Zm | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 64 |  | HydraulicCircuit Zm | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 70 |  | HydraulicCircuit 1 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 71 |  | HydraulicCircuit 1 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 72 |  | HydraulicCircuit 1 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 73 |  | HydraulicCircuit 1 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 74 |  | HydraulicCircuit 1 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 75 |  | HydraulicCircuit 1 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 76 |  | HydraulicCircuit 1 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 77 |  | HydraulicCircuit 1 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 83 |  | HydraulicCircuit 2 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 84 |  | HydraulicCircuit 2 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 85 |  | HydraulicCircuit 2 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 86 |  | HydraulicCircuit 2 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 87 |  | HydraulicCircuit 2 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 88 |  | HydraulicCircuit 2 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 89 |  | HydraulicCircuit 2 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 90 |  | HydraulicCircuit 2 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 96 |  | HydraulicCircuit 3 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 97 |  | HydraulicCircuit 3 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 98 |  | HydraulicCircuit 3 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 99 |  | HydraulicCircuit 3 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 100 |  | HydraulicCircuit 3 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 101 |  | HydraulicCircuit 3 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 102 |  | HydraulicCircuit 3 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 103 |  | HydraulicCircuit 3 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 109 |  | HydraulicCircuit 4 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 110 |  | HydraulicCircuit 4 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 111 |  | HydraulicCircuit 4 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 112 |  | HydraulicCircuit 4 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 113 |  | HydraulicCircuit 4 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 114 |  | HydraulicCircuit 4 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 115 |  | HydraulicCircuit 4 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 116 |  | HydraulicCircuit 4 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 122 |  | HydraulicCircuit 5 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 123 |  | HydraulicCircuit 5 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 124 |  | HydraulicCircuit 5 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 125 |  | HydraulicCircuit 5 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 126 |  | HydraulicCircuit 5 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 127 |  | HydraulicCircuit 5 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 128 |  | HydraulicCircuit 5 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 129 |  | HydraulicCircuit 5 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 135 |  | HydraulicCircuit 6 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 136 |  | HydraulicCircuit 6 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 137 |  | HydraulicCircuit 6 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 138 |  | HydraulicCircuit 6 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 139 |  | HydraulicCircuit 6 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 140 |  | HydraulicCircuit 6 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 141 |  | HydraulicCircuit 6 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 142 |  | HydraulicCircuit 6 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 148 |  | HydraulicCircuit 7 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 149 |  | HydraulicCircuit 7 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 150 |  | HydraulicCircuit 7 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 151 |  | HydraulicCircuit 7 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 152 |  | HydraulicCircuit 7 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 153 |  | HydraulicCircuit 7 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 154 |  | HydraulicCircuit 7 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 155 |  | HydraulicCircuit 7 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 161 |  | HydraulicCircuit 8 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 162 |  | HydraulicCircuit 8 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 163 |  | HydraulicCircuit 8 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 164 |  | HydraulicCircuit 8 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 165 |  | HydraulicCircuit 8 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 166 |  | HydraulicCircuit 8 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 167 |  | HydraulicCircuit 8 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 168 |  | HydraulicCircuit 8 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 174 |  | Mdc | Outdoor temperature | -50 | 200 |  | °C | signed int | x10
HOLDING_REGISTER | Read | 175 |  | Mdc | Damped outdoor temperature |  |  |  | °C | signed int | x10
HOLDING_REGISTER | Read | 176 |  | Mdc | Min Outdoor Temperature | -50 | 0 |  | °C | signed int
HOLDING_REGISTER | Read | 177 |  | Mdc | System flow temperature |  |  |  | °C | signed int | x10
HOLDING_REGISTER | Write | 201 |  | Heat Pump | Heat demand source | 0 | 2 | 0-Scheduler 1-System 2-Max_system_scheduler |  | int
HOLDING_REGISTER | Write | 385 |  | Cascade | Buffer Load On Offset | -10 | 10 |  | K | signed int
HOLDING_REGISTER | Write | 386 |  | Cascade | Buffer Load Off Offset | 1 | 10 |  | K | int
HOLDING_REGISTER | Write | 387 |  | Cascade | Buffer Load Setpoint Offset | 0 | 10 |  | K | int
HOLDING_REGISTER | Write | 388 |  | Cascade | Buffer Load Fast Charge Temperature Setpoint | 30 | 100 |  | °C | int
HOLDING_REGISTER | Write | 389 |  | Cascade | Buffer Load Fast Charge Hysteresis | -10 | -2 |  | K | signed int
HOLDING_REGISTER | Write | 390 |  | Cascade | Buffer Load Minimum Modulation Allowed | 0 | 100 |  | % | int
HOLDING_REGISTER | Write | 391 |  | Cascade | Buffer Load Fast Charge Maximum Runtime | 1 | 24 |  | h | int
HOLDING_REGISTER | Write | 392 |  | Cascade | hrBitblock |  |  |  |  | int
| Write |  | 0 | Cascade | Is Buffer Load Fast Charge Active User |  |  |  |  | bit
| Write |  | 1 | Cascade | Is Buffer Load Fast Charge Start_RE |  |  |  |  | bit
| Write |  | 2 | Cascade | Is Buffer Load Fast Charge Stop_RE |  |  |  |  | bit
HOLDING_REGISTER | Write | 400 |  | Strategy | Temperature Setpoint | 0 | 120 |  | °C | int
HOLDING_REGISTER | Write | 401 |  | Strategy | Power Setpoint | 0 | 100 |  | % | int
HOLDING_REGISTER | Write | 402 |  | Strategy | Working Mode | 0 | 1 | 0-Off 1-On |  | int
HOLDING_REGISTER | Write | 405 |  | Strategy | hrBitblock |  |  |  |  | int
| Write |  | 0 | Strategy | Is Leading |  |  |  |  | bit
| Write |  | 1 | Strategy | Is Priority |  |  |  |  | bit
| Write |  | 2 | Strategy | Is Flow Control Active |  |  |  |  | bit
| Write |  | 3 | Strategy | Is Power Control Active |  |  |  |  | bit
HOLDING_REGISTER | Read | 421 |  | Fresh Water Characteristics 3 | DHU Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 422 |  | Fresh Water Characteristics 3 | Extra Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 423 |  | Fresh Water Characteristics 3 | Maximum DHW Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 424 |  | Fresh Water Characteristics 3 | On High Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 425 |  | Fresh Water Characteristics 3 | On Low Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 426 |  | Fresh Water Characteristics 3 | Fresh Water Type | 0 | 3 | 0-15/20l/min 1-27l/min 2-40l/min 3-60l/min |  | int
HOLDING_REGISTER | Read | 427 |  | Fresh Water Characteristics 3 | Enable Alarm Output | 0 | 2 | 0-No 1-Yes 2-Inverted |  | int
HOLDING_REGISTER | Read | 428 |  | Fresh Water Characteristics 3 | Buffer Cylinder Temperature Offset |  |  |  | K | int
HOLDING_REGISTER | Read | 429 |  | Fresh Water Characteristics 3 | hrBitblock |  |  |  |  | int
| Read |  | 0 | Fresh Water | Buffer Cylinder Temperature Optimization Enabled |  |  |  |  | bit
| Read |  | 1 | Fresh Water | Impulse Enabled |  |  |  |  | bit
| Read |  | 2 | Fresh Water | Time Program Enabled |  |  |  |  | bit
HOLDING_REGISTER | Read | 430 |  | Fresh Water Characteristics 3 | Minimum Buffer Cylinder Temperature Offset |  |  |  | K | int
HOLDING_REGISTER | Read | 431 |  | Fresh Water Characteristics 2 | Circulation Pump Runs per Hour | 0 | 7 | 0-Undefined 1-1x3_minutes/h 2-2x3_minutes/h 3-3x3_minutes/h 4-4x3_minutes/h 5-5x3_minutes/h 6-6x3_minutes/h 7-Permanent |  | int
HOLDING_REGISTER | Read | 432 |  | Fresh Water Characteristics 2 | Swich Hysteresis |  |  |  | K | int
HOLDING_REGISTER | Read | 433 |  | Fresh Water Characteristics 2 | Thermal Disinfection Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 434 |  | Fresh Water Characteristics 2 | Pre Heat Maximum Temperature |  |  |  | °C | int
INPUT_REGISTER | Read | 0 |  | System | Own Outdoor temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1 |  | System | Damped Own outdoor temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4 |  | System | Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5 |  | System | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 7 |  | System | Paired Slaves Bitblock |  |  |  |  | int
| Read |  | 0 | System | Slave 1 Paired |  |  |  |  | bit
| Read |  | 1 | System | Slave 2 Paired |  |  |  |  | bit
| Read |  | 2 | System | Slave 3 Paired |  |  |  |  | bit
| Read |  | 3 | System | Slave 4 Paired |  |  |  |  | bit
| Read |  | 4 | System | Slave 5 Paired |  |  |  |  | bit
| Read |  | 5 | System | Slave 6 Paired |  |  |  |  | bit
| Read |  | 6 | System | Slave 7 Paired |  |  |  |  | bit
| Read |  | 7 | System | Slave 8 Paired |  |  |  |  | bit
| Read |  | 8 | System | Slave 9 Paired |  |  |  |  | bit
| Read |  | 9 | System | Slave 10 Paired |  |  |  |  | bit
| Read |  | 10 | System | Slave 11 Paired |  |  |  |  | bit
| Read |  | 11 | System | Slave 12 Paired |  |  |  |  | bit
| Read |  | 12 | System | Slave 13 Paired |  |  |  |  | bit
| Read |  | 13 | System | Slave 14 Paired |  |  |  |  | bit
| Read |  | 14 | System | Slave 15 Paired |  |  |  |  | bit
INPUT_REGISTER | Read | 8 |  | System | Active Functions 1 |  |  |  |  | int
| Read |  | 0 | System | HC 0 Active |  |  |  |  | bit
| Read |  | 1 | System | HC 1 Active |  |  |  |  | bit
| Read |  | 2 | System | HC 2 Active |  |  |  |  | bit
| Read |  | 3 | System | HC 3 Active |  |  |  |  | bit
| Read |  | 4 | System | HC 4 Active |  |  |  |  | bit
| Read |  | 5 | System | HC 5 Active |  |  |  |  | bit
| Read |  | 6 | System | HC 6 Active |  |  |  |  | bit
| Read |  | 7 | System | HC 7 Active |  |  |  |  | bit
| Read |  | 8 | System | HC 8 Active |  |  |  |  | bit
| Read |  | 9 | System | DHW 1 Active |  |  |  |  | bit
| Read |  | 10 | System | DHW 2 Active |  |  |  |  | bit
| Read |  | 11 | System | AHS Active |  |  |  |  | bit
| Read |  | 12 | System | CHP Active |  |  |  |  | bit
| Read |  | 13 | System | Safety Chain Active |  |  |  |  | bit
| Read |  | 14 | System | Water Treatment Active |  |  |  |  | bit
| Read |  | 15 | System | Solar Active |  |  |  |  | bit
INPUT_REGISTER | Read | 9 |  | System | Active Functions 2 |  |  |  |  | int
| Read |  | 0 | System | Fresh Water Active |  |  |  |  | bit
| Read |  | 1 | System | Function 18 Active |  |  |  |  | bit
| Read |  | 2 | System | Function 19 Active |  |  |  |  | bit
| Read |  | 3 | System | Function 20 Active |  |  |  |  | bit
| Read |  | 4 | System | Function 21 Active |  |  |  |  | bit
| Read |  | 5 | System | Function 22 Active |  |  |  |  | bit
| Read |  | 6 | System | Function 23 Active |  |  |  |  | bit
| Read |  | 7 | System | Function 24 Active |  |  |  |  | bit
| Read |  | 8 | System | Function 25 Active |  |  |  |  | bit
| Read |  | 9 | System | Function 26 Active |  |  |  |  | bit
| Read |  | 10 | System | Function 27 Active |  |  |  |  | bit
| Read |  | 11 | System | Function 28 Active |  |  |  |  | bit
| Read |  | 12 | System | Function 29 Active |  |  |  |  | bit
| Read |  | 13 | System | Function 30 Active |  |  |  |  | bit
| Read |  | 14 | System | Function 31 Active |  |  |  |  | bit
| Read |  | 15 | System | Function 32 Active |  |  |  |  | bit
INPUT_REGISTER | Read | 15 |  | DomesticHotWater Zm | Charge Pump Running | 0 | 4 | 0-Stopping 1-Starting 2-Running 3-Off 4-Error |  | int
INPUT_REGISTER | Read | 16 |  | DomesticHotWater Zm | Circulation Pump Running | 0 | 4 | 0-Stopping 1-Starting 2-Running 3-Off 4-Error |  | int
INPUT_REGISTER | Read | 17 |  | DomesticHotWater Zm | Hydraulic State | 0 | 7 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Cold_load 6-Post_purge 7-Condense_protection |  | int
INPUT_REGISTER | Read | 18 |  | DomesticHotWater Zm/Ems | Thermal Disinfection Status | 0 | 3 | 0-Off 1-On 2-Success 3-Error |  | int
INPUT_REGISTER | Read | 19 |  | DomesticHotWater Zm/Ems | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 20 |  | DomesticHotWater Zm/Ems | Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 21 |  | DomesticHotWater Zm/Ems | Current Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 31 |  | DomesticHotWater Fm | Charge Pump Running | 0 | 4 | 0-Stopping 1-Starting 2-Running 3-Off 4-Error |  | int
INPUT_REGISTER | Read | 32 |  | DomesticHotWater Fm | Circulation Pump Running | 0 | 4 | 0-Stopping 1-Starting 2-Running 3-Off 4-Error |  | int
INPUT_REGISTER | Read | 33 |  | DomesticHotWater Fm | Hydraulic State | 0 | 7 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Cold_load 6-Post_purge 7-Condense_protection |  | int
INPUT_REGISTER | Read | 34 |  | DomesticHotWater Fm | Thermal Disinfection Status | 0 | 3 | 0-Off 1-On 2-Success 3-Error |  | int
INPUT_REGISTER | Read | 35 |  | DomesticHotWater Fm | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 36 |  | DomesticHotWater Fm | Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 37 |  | DomesticHotWater Fm | Current Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER |  | 47 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 48 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 50 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 52 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 53 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 54 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 55 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 56 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 59 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 60 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER | Read | 63 |  | AlternativeHeatSource | Operating hours |  |  |  | h | long
INPUT_REGISTER | Read | 65 |  | AlternativeHeatSource | Heat Source Starts |  |  |  |  | long
INPUT_REGISTER | Read | 67 |  | AlternativeHeatSource | Heat Source Hours to Maintenance |  |  |  | h | int
INPUT_REGISTER | Read | 69 |  | AlternativeHeatSource | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 70 |  | AlternativeHeatSource | irBitblock |  |  |  |  | int
| Read |  | 0 | AlternativeHeatSource | Is Heat Source On |  |  |  |  | bit
| Read |  | 1 | AlternativeHeatSource | Is Heat Source On Request |  |  |  |  | bit
INPUT_REGISTER | Read | 71 |  | AlternativeHeatSource | System Return Temperature FAR |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 72 |  | AlternativeHeatSource | Buffer Middle Temperature FPM |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 73 |  | AlternativeHeatSource | Buffer Top Temperature FPO |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 74 |  | AlternativeHeatSource | Buffer Bottom Temperature FPU |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 75 |  | AlternativeHeatSource | Exhaust Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 76 |  | AlternativeHeatSource | Return Temperature FWR |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 77 |  | AlternativeHeatSource | Flow Temperature FWV |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 78 |  | AlternativeHeatSource | Mixer Position |  |  |  | % | int
INPUT_REGISTER | Read | 79 |  | AlternativeHeatSource | SWE Bypass Position | 0 | 6 | 0-Idle 1-Is_Closing 2-Is_Opening 3-Fully_Opened 4-Fully_Closed 5-Pump_On 6-Pump_Off |  | int
INPUT_REGISTER | Read | 87 |  | HydraulicCircuit Zm | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 88 |  | HydraulicCircuit Zm | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 89 |  | HydraulicCircuit Zm | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 90 |  | HydraulicCircuit Zm | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 91 |  | HydraulicCircuit Zm | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 92 |  | HydraulicCircuit Zm | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 93 |  | HydraulicCircuit Zm | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 94 |  | HydraulicCircuit Zm | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 95 |  | HydraulicCircuit Zm | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 99 |  | HydraulicCircuit 1 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 100 |  | HydraulicCircuit 1 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 101 |  | HydraulicCircuit 1 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 102 |  | HydraulicCircuit 1 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 103 |  | HydraulicCircuit 1 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 104 |  | HydraulicCircuit 1 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 105 |  | HydraulicCircuit 1 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 106 |  | HydraulicCircuit 1 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 107 |  | HydraulicCircuit 1 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 112 |  | HydraulicCircuit 2 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 113 |  | HydraulicCircuit 2 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 114 |  | HydraulicCircuit 2 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 115 |  | HydraulicCircuit 2 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 116 |  | HydraulicCircuit 2 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 117 |  | HydraulicCircuit 2 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 118 |  | HydraulicCircuit 2 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 119 |  | HydraulicCircuit 2 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 120 |  | HydraulicCircuit 2 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 125 |  | HydraulicCircuit 3 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 126 |  | HydraulicCircuit 3 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 127 |  | HydraulicCircuit 3 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 128 |  | HydraulicCircuit 3 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 129 |  | HydraulicCircuit 3 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 130 |  | HydraulicCircuit 3 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 131 |  | HydraulicCircuit 3 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 132 |  | HydraulicCircuit 3 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 133 |  | HydraulicCircuit 3 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 138 |  | HydraulicCircuit 4 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 139 |  | HydraulicCircuit 4 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 140 |  | HydraulicCircuit 4 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 141 |  | HydraulicCircuit 4 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 142 |  | HydraulicCircuit 4 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 143 |  | HydraulicCircuit 4 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 144 |  | HydraulicCircuit 4 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 145 |  | HydraulicCircuit 4 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 146 |  | HydraulicCircuit 4 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 151 |  | HydraulicCircuit 5 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 152 |  | HydraulicCircuit 5 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 153 |  | HydraulicCircuit 5 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 154 |  | HydraulicCircuit 5 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 155 |  | HydraulicCircuit 5 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 156 |  | HydraulicCircuit 5 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 157 |  | HydraulicCircuit 5 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 158 |  | HydraulicCircuit 5 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 159 |  | HydraulicCircuit 5 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 164 |  | HydraulicCircuit 6 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 165 |  | HydraulicCircuit 6 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 166 |  | HydraulicCircuit 6 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 167 |  | HydraulicCircuit 6 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 168 |  | HydraulicCircuit 6 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 169 |  | HydraulicCircuit 6 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 170 |  | HydraulicCircuit 6 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 171 |  | HydraulicCircuit 6 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 172 |  | HydraulicCircuit 6 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 177 |  | HydraulicCircuit 7 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 178 |  | HydraulicCircuit 7 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 179 |  | HydraulicCircuit 7 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 180 |  | HydraulicCircuit 7 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 181 |  | HydraulicCircuit 7 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 182 |  | HydraulicCircuit 7 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 183 |  | HydraulicCircuit 7 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 184 |  | HydraulicCircuit 7 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 185 |  | HydraulicCircuit 7 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 190 |  | HydraulicCircuit 8 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 191 |  | HydraulicCircuit 8 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 192 |  | HydraulicCircuit 8 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 193 |  | HydraulicCircuit 8 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 194 |  | HydraulicCircuit 8 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 195 |  | HydraulicCircuit 8 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 196 |  | HydraulicCircuit 8 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 197 |  | HydraulicCircuit 8 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 198 |  | HydraulicCircuit 8 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 203 |  | i2c | Global Error State | 0 | 4 | 0-No_Error 1-i2c_driver_error 2-Wrong_Cycle_Time 3-Missing_Module_Slot 4-Module_Slot_Error |  | int
INPUT_REGISTER | Read | 204 |  | i2c | Slot1 Module Detected |  |  | 0-Unknown 1-None 22-FM_CM 25-FM_SI 28-FM_MM 29-FM_MW 30-FM_AM 31-FM_CM2 |  | int
INPUT_REGISTER | Read | 205 |  | i2c | Slot1 Error State |  |  | 0-No_Error 1-No_Response 2-Wrong_Module 3-Unsupported_Module 4-Internal_Sw_Error 5-Communication_Failed 6-Internal_Module_Error 7-Module_Not_Supported_Current_Variant 8-Module_Not_Suppported_In_Slot 9-Module_Count_Too_High 10-Module_Not_Supported_With_Connected_Boiler_Type |  | int
INPUT_REGISTER | Read | 206 |  | i2c | Slot2 Module Detected |  |  | 0-Unknown 1-None 22-FM_CM 25-FM_SI 28-FM_MM 29-FM_MW 30-FM_AM 31-FM_CM2 |  | int
INPUT_REGISTER | Read | 207 |  | i2c | Slot2 Error State |  |  | 0-No_Error 1-No_Response 2-Wrong_Module 3-Unsupported_Module 4-Internal_Sw_Error 5-Communication_Failed 6-Internal_Module_Error 7-Module_Not_Supported_Current_Variant 8-Module_Not_Suppported_In_Slot 9-Module_Count_Too_High 10-Module_Not_Supported_With_Connected_Boiler_Type |  | int
INPUT_REGISTER | Read | 208 |  | i2c | Slot3 Module Detected |  |  | 0-Unknown 1-None 22-FM_CM 25-FM_SI 28-FM_MM 29-FM_MW 30-FM_AM 31-FM_CM2 |  | int
INPUT_REGISTER | Read | 209 |  | i2c | Slot3 Error State |  |  | 0-No_Error 1-No_Response 2-Wrong_Module 3-Unsupported_Module 4-Internal_Sw_Error 5-Communication_Failed 6-Internal_Module_Error 7-Module_Not_Supported_Current_Variant 8-Module_Not_Suppported_In_Slot 9-Module_Count_Too_High 10-Module_Not_Supported_With_Connected_Boiler_Type |  | int
INPUT_REGISTER | Read | 210 |  | i2c | Slot4 Module Detected |  |  | 0-Unknown 1-None 22-FM_CM 25-FM_SI 28-FM_MM 29-FM_MW 30-FM_AM 31-FM_CM2 |  | int
INPUT_REGISTER | Read | 211 |  | i2c | Slot4 Error State |  |  | 0-No_Error 1-No_Response 2-Wrong_Module 3-Unsupported_Module 4-Internal_Sw_Error 5-Communication_Failed 6-Internal_Module_Error 7-Module_Not_Supported_Current_Variant 8-Module_Not_Suppported_In_Slot 9-Module_Count_Too_High 10-Module_Not_Supported_With_Connected_Boiler_Type |  | int
INPUT_REGISTER | Read | 212 |  | i2c | Slot A Module Detected |  |  | 0-Unknown 1-None 26-ZM5313 27-ZM5311 |  | int
INPUT_REGISTER | Read | 213 |  | i2c | Slot A Error State |  |  | 0-No_Error 1-No_Response 2-Wrong_Module 3-Unsupported_Module 4-Internal_Sw_Error 5-Communication_Failed 6-Internal_Module_Error 7-Module_Not_Supported_Current_Variant 8-Module_Not_Suppported_In_Slot 9-Module_Count_Too_High 10-Module_Not_Supported_With_Connected_Boiler_Type |  | int
INPUT_REGISTER | Read | 214 |  | i2c | irBitblock |  |  |  |  | int
| Read |  | 0 | i2c | Component Error |  |  |  |  | bit
INPUT_REGISTER | Read | 225 |  | fm-si | irBitblock |  |  |  |  | int
| Read |  | 0 | fm-si | Input 1 Error |  |  |  |  | bit
| Read |  | 1 | fm-si | Input 2 Error |  |  |  |  | bit
| Read |  | 2 | fm-si | Input 3 Error |  |  |  |  | bit
| Read |  | 3 | fm-si | Input 4 Error |  |  |  |  | bit
| Read |  | 4 | fm-si | Input 5 Error |  |  |  |  | bit
INPUT_REGISTER | Read | 232 |  | Sdc | Demand Mode (Low Priority) | 0 | 2 | 0-Off 1-Take_Heat 2-Give_Heat |  | int
INPUT_REGISTER | Read | 233 |  | Sdc | Demand Flow Temp (Low Priority) |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 234 |  | Sdc | Demand Mode (High Priority) | 0 | 2 | 0-Off 1-Take_Heat 2-Give_Heat |  | int
INPUT_REGISTER | Read | 235 |  | Sdc | Demand Flow Temp (High Priority) |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 239 |  | Heat Pump | System return temperature for HP heating buffer |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 240 |  | Heat Pump | Buffer mid temperature for HP heating buffer |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 241 |  | Heat Pump | Buffer top temperature for HP heating buffer |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 242 |  | Heat Pump | Buffer bottom temperature for HP heating buffer |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 243 |  | Heat Pump | Return temperature FWR |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 244 |  | Heat Pump | Flow temperature FWV |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 245 |  | Heat Pump | Flow temperature HP |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 246 |  | Heat Pump | Return temperature HP |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 247 |  | Heat Pump | HMI State of HP Component | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 248 |  | Heat Pump | HP current heat output |  |  |  | kW | signed int | x10
INPUT_REGISTER | Read | 249 |  | Heat Pump | HP current electrical power consumption | 0 | 10000 |  | kW | int | x10
INPUT_REGISTER | Read | 250 |  | Heat Pump | HP Smart grid mode | 0 | 3 | 0-normal_charging_grid 1-low_charging_grid 2-high_charging_grid 3-free_charging_grid |  | int
INPUT_REGISTER | Read | 251 |  | Heat Pump | Heat demand temperature set point |  |  |  | °C | int
INPUT_REGISTER | Read | 252 |  | Heat Pump | heatPumpStatusIrBitblock | 0 |  |  |  | int
INPUT_REGISTER | Read | 253 |  | Heat Pump | Ambient Temperature HP |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 254 |  | Heat Pump | HP silent mode | 0 | 3 | 0-standard_mode 1-silent_mode 2-super_silent_mode 3-night_mode |  | int
INPUT_REGISTER | Read | 255 |  | Heat Pump | Heat Pump Heat Request Temperature |  |  |  | °C | int
INPUT_REGISTER | Read | 256 |  | Heat Pump | heatPumpIrBitblock |  |  |  |  | int
INPUT_REGISTER | Read | 265 |  | System | Open Notifications Count |  |  |  |  | int
INPUT_REGISTER | Read | 266 |  | System | Error Key 5 |  |  |  |  | long
INPUT_REGISTER | Read | 268 |  | System | Error Key 6 |  |  |  |  | long
INPUT_REGISTER | Read | 270 |  | System | Error Key 7 |  |  |  |  | long
INPUT_REGISTER | Read | 272 |  | System | Error Key 8 |  |  |  |  | long
INPUT_REGISTER | Read | 274 |  | System | Error Key 9 |  |  |  |  | long
INPUT_REGISTER | Read | 276 |  | System | Error Key 10 |  |  |  |  | long
INPUT_REGISTER | Read | 278 |  | Chp / EC Power | Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 279 |  | Chp / EC Power | Return Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 280 |  | Chp | Flue Gas Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 281 |  | Chp | Motor Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 282 |  | Chp / EC Power | Current Generator Power |  |  |  | kW | int
INPUT_REGISTER | Read | 283 |  | Chp | Current Power Setpoint |  |  |  | kW | int
INPUT_REGISTER | Read | 284 |  | Chp / EC Power | Operation Hours |  |  |  | h | long
INPUT_REGISTER | Read | 286 |  | Chp / EC Power | Number of starts |  |  |  |  | long
INPUT_REGISTER | Read | 288 |  | Chp / EC Power | Hours to Maintenance |  |  |  | h | int
INPUT_REGISTER | Read | 290 |  | Chp | Output Power Setpoint |  |  |  | kW | int
INPUT_REGISTER | Read | 291 |  | Chp | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 296 |  | Chp | irBitblock |  |  |  |  | int
| Read |  | 0 | Chp | Warning |  |  |  |  | bit
| Read |  | 1 | Chp / EC Power | Malfunction |  |  |  |  | bit
| Read |  | 2 | Chp / EC Power | Controlled Shutdown |  |  |  |  | bit
| Read |  | 3 | Chp / EC Power | Generator On |  |  |  |  | bit
| Read |  | 4 | Chp | Automatic On |  |  |  |  | bit
| Read |  | 5 | Chp / EC Power | Automatic Ready |  |  |  |  | bit
| Read |  | 11 | Chp / EC Power | Output On Request |  |  |  |  | bit
INPUT_REGISTER | Read | 304 |  | Water Treatment Module | Program Step |  |  | 20-140: Desalination not active 10000-10810: One time desalination 20000-20810: Automatic desalination 30000-30260: Stationary operation |  | int
INPUT_REGISTER | Read | 305 |  | Water Treatment Module | Temperature Desalinization |  |  |  | °C | int | x10
INPUT_REGISTER | Read | 306 |  | Water Treatment Module | Volume Flow |  |  |  | L/min | int | x10
INPUT_REGISTER | Read | 307 |  | Water Treatment Module | Conductivity system |  |  |  | uS/cm | int | x10
INPUT_REGISTER | Read | 308 |  | Water Treatment Module | Conductivity cartridge |  |  |  | uS/cm | int | x10
INPUT_REGISTER | Read | 309 |  | Water Treatment Module | Cartridge Capacity |  |  |  | % | int
INPUT_REGISTER | Read | 313 |  | Solar Data | Collector temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 314 |  | Solar Data | Temperature cylinder bottom |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 315 |  | Solar Data | Solar pump modulation setpoint |  |  |  | % | int
INPUT_REGISTER | Read | 316 |  | Solar | Solar pump status | 0 | 19 | 1-TestMod 2-BlckProt 3-No heat 4-Ht avail 5-SolOff 6-MaxCyl 7-MaxColl 8-MinColl 9-FrostP 10-VacFct 11-SwChck 12-MixPrio 13-Switch 14-Priority 15-ThermD 16-MixCal 17-MixOpn 18-MixCl 19-MixOff |  | int
INPUT_REGISTER | Read | 317 |  | Solar Data | Heat exchanger temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 318 |  | Solar Data | Heat exchanger pump modulation setpoint |  |  |  | % | int
INPUT_REGISTER | Read | 319 |  | Solar | Heat exchanger pump status | 0 | 19 | 1-TestMod 2-BlckProt 3-No heat 4-Ht avail 5-SolOff 6-MaxCyl 7-MaxColl 8-MinColl 9-FrostP 10-VacFct 11-SwChck 12-MixPrio 13-Switch 14-Priority 15-ThermD 16-MixCal 17-MixOpn 18-MixCl 19-MixOff |  | int
INPUT_REGISTER | Read | 320 |  | Solar Data | Temperature cylinder 3 top |  |  |  | °C | int | x10
INPUT_REGISTER | Read | 321 |  | Solar Data | Reload pump modulation setpoint |  |  |  | % | int
INPUT_REGISTER | Read | 322 |  | Solar | Reload pump status | 0 | 19 | 1-TestMod 2-BlckProt 3-No heat 4-Ht avail 5-SolOff 6-MaxCyl 7-MaxColl 8-MinColl 9-FrostP 10-VacFct 11-SwChck 12-MixPrio 13-Switch 14-Priority 15-ThermD 16-MixCal 17-MixOpn 18-MixCl 19-MixOff |  | int
INPUT_REGISTER | Read | 323 |  | Solar | Pump therm. disinfect. status | 0 | 19 | 1-TestMod 2-BlckProt 3-No heat 4-Ht avail 5-SolOff 6-MaxCyl 7-MaxColl 8-MinColl 9-FrostP 10-VacFct 11-SwChck 12-MixPrio 13-Switch 14-Priority 15-ThermD 16-MixCal 17-MixOpn 18-MixCl 19-MixOff |  | int
INPUT_REGISTER | Read | 324 |  | Solar Yield | Flow temperature heat meter |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 325 |  | Solar Yield | Return temperature heat meter |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 326 |  | Solar Yield | Heat count pulse counter | 0 | 15 |  |  | int
INPUT_REGISTER | Read | 327 |  | Solar Yield | Solar yield per month |  |  |  | kWh | long | x10
INPUT_REGISTER | Read | 329 |  | Solar Yield | Solar yield per year |  |  |  | kWh | long | x10
INPUT_REGISTER | Read | 331 |  | Solar Yield | Last hour solar yield |  |  |  | kWh | long | x10
INPUT_REGISTER | Read | 333 |  | Solar Yield | Solar yield per day |  |  |  | kWh | long | x10
INPUT_REGISTER | Read | 335 |  | Solar Yield | Solar yield since installation |  |  |  | kWh | long | x10
INPUT_REGISTER | Read | 337 |  | Solar | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 338 |  | Solar Data | Hydraulic configuration |  |  |  |  | int
| Read |  | 0 | Solar | Option 1 active |  |  |  |  | bit
| Read |  | 1 | Solar | Option A active |  |  |  |  | bit
| Read |  | 2 | Solar | Option B active |  |  |  |  | bit
| Read |  | 3 | Solar | Option C active |  |  |  |  | bit
| Read |  | 4 | Solar | Option D active |  |  |  |  | bit
| Read |  | 5 | Solar | Option E active |  |  |  |  | bit
| Read |  | 6 | Solar | Option F active |  |  |  |  | bit
| Read |  | 7 | Solar | Option G active |  |  |  |  | bit
| Read |  | 8 | Solar | Option H active |  |  |  |  | bit
| Read |  | 9 | Solar | Option I active |  |  |  |  | bit
| Read |  | 10 | Solar | Option J active |  |  |  |  | bit
| Read |  | 11 | Solar | Option K active |  |  |  |  | bit
| Read |  | 12 | Solar | Option L active |  |  |  |  | bit
| Read |  | 13 | Solar | Option M active |  |  |  |  | bit
| Read |  | 14 | Solar | Option N active |  |  |  |  | bit
| Read |  | 15 | Solar | Option P active |  |  |  |  | bit
INPUT_REGISTER | Read | 339 |  | Solar Data | irBitblock |  |  |  |  | int
| Read |  | 0 | Solar | Is Active |  |  |  |  | bit
INPUT_REGISTER | Read | 360 |  | Cascade | Boilers Active |  |  |  |  | int
INPUT_REGISTER | Read | 361 |  | Cascade | Boilers Under Control |  |  |  |  | int
INPUT_REGISTER | Read | 362 |  | Cascade | Boilers Allowed to Run |  |  |  |  | int
INPUT_REGISTER | Read | 363 |  | Cascade | Total Power |  |  |  | kW | int
INPUT_REGISTER | Read | 364 |  | Cascade | Power Under Control |  |  |  | kW | int
INPUT_REGISTER | Read | 365 |  | Cascade | Current Power |  |  |  | kW | int
INPUT_REGISTER | Read | 366 |  | Cascade | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 367 |  | Cascade | Current Request Operation Mode | 0 | 4 | 0-Off 1-Temperature_Control 2-Integral 3-Temperature_Power_Control 4-Power_Control |  | int
INPUT_REGISTER | Read | 370 |  | Cascade | Buffer Load Power Request |  |  |  | % | int | x10
INPUT_REGISTER | Read | 371 |  | Cascade | Buffer Load Temperature Request Setpoint |  |  |  | °C | signed int
INPUT_REGISTER | Read | 372 |  | Cascade | Buffer Load Minimum Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 373 |  | Cascade | Buffer Load Auto Charge On Threshold |  |  |  | °C | signed int
INPUT_REGISTER | Read | 374 |  | Cascade | Buffer Load Auto Charge Off Threshold |  |  |  | °C | signed int
INPUT_REGISTER | Read | 375 |  | Cascade | irBitblock |  |  |  |  | int
| Read |  | 0 | Cascade | Is Buffer Load Auto Charge On Request |  |  |  |  | bit
| Read |  | 1 | Cascade | Is Buffer Load Fast Charge On Request |  |  |  |  | bit
INPUT_REGISTER | Read | 384 |  | System | Return Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 385 |  | System | System Flow / LLH Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 386 |  | Strategy | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 387 |  | System | Actual Power |  |  |  | % | int
INPUT_REGISTER | Read | 388 |  | Strategy | Source Load | 0 | 3 | 0-Ahs 1-Cascade 2-None 3-Substation |  | int
INPUT_REGISTER | Read | 389 |  | Strategy | Llh Increase Value |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 390 |  | Strategy | Request Source | 0 | 5 | 0-NotActive 1-Hardware 2-Intern 3-Manual 4-Extern 5-Intern_Extern |  | int
INPUT_REGISTER | Read | 391 |  | Strategy | Request Flow Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 392 |  | Strategy | Request Power Setpoint |  |  |  | % | int
INPUT_REGISTER | Read | 393 |  | Strategy | Request Mode | 0 | 2 | 0-Off 1-Take_Heat 2-Give_Heat |  | int
INPUT_REGISTER | Read | 394 |  | Strategy | irBitblock |  |  |  |  | int
| Read |  | 0 | Strategy | Is External Heat Detected |  |  |  |  | bit
| Read |  | 1 | Strategy | Is Anti Freeze Heat Request |  |  |  |  | bit
| Read |  | 2 | Strategy | Is Request Priority |  |  |  |  | bit
| Read |  | 3 | Strategy | Is Request Leading |  |  |  |  | bit
| Read |  | 4 | Strategy | Is Request Flow Control Active |  |  |  |  | bit
| Read |  | 5 | Strategy | Is Request Power Control Active |  |  |  |  | bit
| Read |  | 6 | Strategy | Is External Control Possible |  |  |  |  | bit
INPUT_REGISTER | Read | 395 |  | Strategy | Request Flow Max Temp Setpoint |  |  |  | °C | signed int
INPUT_REGISTER |  | 400 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 401 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 402 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 403 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 404 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 405 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 406 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 407 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 408 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 409 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 410 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 411 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 412 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 413 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER | Read | 422 |  | Energy Monitoring | Heat Output |  |  |  | kW | signed int | x10
INPUT_REGISTER | Read | 423 |  | Energy Monitoring | Gas Consumption (LCV) |  |  |  | kW | signed int | x10
INPUT_REGISTER | Read | 425 |  | Energy Monitoring | Electrical Power |  |  |  | W | int
INPUT_REGISTER | Read | 430 |  | Fresh Water Characteristics 1 | DHW Out Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 431 |  | Fresh Water Characteristics 1 | DHW Volume Flow |  |  |  | L/min | signed int | x10
INPUT_REGISTER | Read | 432 |  | Fresh Water Characteristics 1 | Prim In Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 433 |  | Fresh Water Characteristics 1 | DHW In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 434 |  | Fresh Water Characteristics 1 | Primary Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 435 |  | Fresh Water Characteristics 1 | Request DHW Out Temperature |  |  |  | °C | int
INPUT_REGISTER | Read | 436 |  | Fresh Water Characteristics 1 | Status Request DHW Out Temperature | 0 | 9 | 0-Off 1-DHWRed 2-DHW 3-Sol_red 4-Once_on 5-Therm_d 6-DlyHtUp 7-Preheat_start 8-Preheat_normal 9-No_eq |  | int
INPUT_REGISTER | Read | 437 |  | Fresh Water Characteristics 2 | Circulation Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 438 |  | Fresh Water Characteristics 2 | Status Circulation Pump | 0 | 8 | 0-Undefined 1-Test 2-BlckProt 3-No_req 4-AutoOff 5-AutoOn 6-Therm_d 7-Sys_Off 8-DlyHtUp |  | int
INPUT_REGISTER | Read | 439 |  | Fresh Water Characteristics 2 | Return Valve Modulation Request |  |  |  | % | int
INPUT_REGISTER | Read | 440 |  | Fresh Water Characteristics 2 | Valve State | 0 | 5 | 0-Undefined 1-TestMod 2-BlckProt 3-Mix_cl 4-Mix_opn 5-Sys_Off |  | int
INPUT_REGISTER | Read | 441 |  | Fresh Water Characteristics 2 | Return Valve Buffer Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 442 |  | Fresh Water Characteristics 2 | Disinfection Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 443 |  | Fresh Water Characteristics 2 | Pump State | 0 | 5 | 0-Undefined 1-TestMod 2-BlckPro 3-No_eq 4-Ht_req 5-Sys_Off |  | int
INPUT_REGISTER | Read | 444 |  | Fresh Water Characteristics 1 | DHW Valve Power |  |  |  | % | int
INPUT_REGISTER | Read | 445 |  | Fresh Water Characteristics 2 | Total Flow |  |  |  | L/min | int | x10
INPUT_REGISTER | Read | 446 |  | Fresh Water 2 | Module 2 DHW Out Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 447 |  | Fresh Water 2 | Module 2 DHW Volume Flow |  |  |  | L/min | signed int | x10
INPUT_REGISTER | Read | 448 |  | Fresh Water 2 | Module 2 Prim In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 449 |  | Fresh Water 2 | Module 2 DHW In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 450 |  | Fresh Water 2 | Module 2 DHW Valve Power |  |  |  | % | int
INPUT_REGISTER | Read | 451 |  | Fresh Water 2 | Module 2 Prim Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 452 |  | Fresh Water 2 | Module 2 Status Prim Pump |  |  |  |  | int
INPUT_REGISTER | Read | 453 |  | Fresh Water 3 | Module 3 DHW Out Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 454 |  | Fresh Water 3 | Module 3 DHW Volume Flow |  |  |  | L/min | signed int | x10
INPUT_REGISTER | Read | 455 |  | Fresh Water 3 | Module 3 Prim In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 456 |  | Fresh Water 3 | Module 3 DHW In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 457 |  | Fresh Water 3 | Module 3 DHW Valve Power |  |  |  | % | int
INPUT_REGISTER | Read | 458 |  | Fresh Water 3 | Module 3 Prim Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 459 |  | Fresh Water 3 | Module 3 Status Prim Pump |  |  |  |  | int
INPUT_REGISTER | Read | 460 |  | Fresh Water 4 | Module 4 DHW Out Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 461 |  | Fresh Water 4 | Module 4 DHW Volume Flow |  |  |  | L/min | signed int | x10
INPUT_REGISTER | Read | 462 |  | Fresh Water 4 | Module 4 Prim In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 463 |  | Fresh Water 4 | Module 4 DHW In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 464 |  | Fresh Water 4 | Module 4 DHW ValvePower |  |  |  | % | int
INPUT_REGISTER | Read | 465 |  | Fresh Water 4 | Module 4 Prim Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 466 |  | Fresh Water 4 | Module 4 Status Primary Pump |  |  |  |  | int
INPUT_REGISTER | Read | 467 |  | Fresh Water | Fresh Water Hmi State |  |  |  |  | int
INPUT_REGISTER | Read | 468 |  | Fresh Water Characteristics 3 | Fresh Water Configurations |  |  |  |  | int
| Read |  | 0 | Fresh Water | Option 2 active |  |  |  |  | bit
| Read |  | 1 | Fresh Water | Option A active |  |  |  |  | bit
| Read |  | 2 | Fresh Water | Option B active |  |  |  |  | bit
| Read |  | 3 | Fresh Water | Option C active |  |  |  |  | bit
| Read |  | 4 | Fresh Water | Option D active |  |  |  |  | bit
| Read |  | 5 | Fresh Water | Option E active |  |  |  |  | bit
| Read |  | 6 | Fresh Water | Option E active cascade module 2 active |  |  |  |  | bit
| Read |  | 7 | Fresh Water | Option E active cascade module 3 active |  |  |  |  | bit
| Read |  | 8 | Fresh Water | Option E active cascade module 4 active |  |  |  |  | bit
| Read |  | 9 | Fresh Water | Is Active |  |  |  |  | bit
INPUT_REGISTER | Read | 476 |  | System | Error Key 1 |  |  |  |  | long
INPUT_REGISTER | Read | 478 |  | System | Error Key 2 |  |  |  |  | long
INPUT_REGISTER | Read | 480 |  | System | Error Key 3 |  |  |  |  | long
INPUT_REGISTER | Read | 482 |  | System | Error Key 4 |  |  |  |  | long
INPUT_REGISTER | Read | 484 |  | System | Error 1 Extra Info (MSB) |  |  |  |  | long
INPUT_REGISTER | Read | 486 |  | System | Error 1 Extra Info (LSB) |  |  |  |  | long
INPUT_REGISTER | Read | 488 |  | System | Error 2 Extra Info (MSB) |  |  |  |  | long
INPUT_REGISTER | Read | 490 |  | System | Error 2 Extra Info (LSB) |  |  |  |  | long
INPUT_REGISTER | Read | 492 |  | System | Error 3 Extra Info (MSB) |  |  |  |  | long
INPUT_REGISTER | Read | 494 |  | System | Error 3 Extra Info (LSB) |  |  |  |  | long
INPUT_REGISTER | Read | 496 |  | System | Error 4 Extra Info (MSB) |  |  |  |  | long
INPUT_REGISTER | Read | 498 |  | System | Error 4 Extra Info (LSB) |  |  |  |  | long
INPUT_REGISTER | Read | 8000 |  | Boiler1 | Boiler Type |  |  | 0-None 1-EMS 2-SAFe 3-SEVEN_POLE 4-SLAVE_CBC |  | int
INPUT_REGISTER | Read | 8001 |  | Boiler1 | Flow temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 8002 |  | Boiler1 | Flow temperature rate of change |  |  |  | K/min | signed int | x10
INPUT_REGISTER | Read | 8003 |  | Boiler1 | Return Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 8004 |  | Boiler1 | Current power |  |  |  | % | int
INPUT_REGISTER | Read | 8005 |  | Boiler1 | Load limit continuous |  |  |  | % | int
INPUT_REGISTER | Read | 8006 |  | Boiler1 | Operating temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 8007 |  | Boiler1 | Maximum power |  |  |  | kW | int
INPUT_REGISTER | Read | 8008 |  | Boiler1 | Minimum relative power |  |  |  | % | int
INPUT_REGISTER | Read | 8009 |  | Boiler1 | Burner type |  |  | 0-Modulating 1-One_Stage 2-Two_Stage |  | int
INPUT_REGISTER | Read | 8010 |  | Boiler1 | Fuel type |  |  | 0-Gas 1-Oil |  | int
INPUT_REGISTER | Read | 8011 |  | Boiler1 | Maximum Temp Setpoint |  |  |  | °C | int
INPUT_REGISTER | Read | 8012 |  | Boiler1 | Hmi State |  |  | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 8013 |  | Boiler1 | bitblock |  |  |  |  | int
| Read |  | 0 | Boiler1 | isControlPossible |  |  |  |  | bit
| Read |  | 1 | Boiler1 | isForcedFlow |  |  |  |  | bit
| Read |  | 2 | Boiler1 | isTakeHeat |  |  |  |  | bit
| Read |  | 3 | Boiler1 | isLoadLimitDigital |  |  |  |  | bit
| Read |  | 4 | Boiler1 | isLoadLimitFastReduction |  |  |  |  | bit
| Read |  | 5 | Boiler1 | isBurnerOn |  |  |  |  | bit
| Read |  | 6 | Boiler1 | isRequestLeading |  |  |  |  | bit
| Read |  | 7 | Boiler1 | isRequestPriority |  |  |  |  | bit
| Read |  | 8 | Boiler1 | isRequestFlowControl |  |  |  |  | bit
| Read |  | 9 | Boiler1 | isRequestPowerControl |  |  |  |  | bit
| Read |  | 10 | Boiler1 | isLocked |  |  |  |  | bit
| Read |  | 11 | Boiler1 | isBlocked |  |  |  |  | bit
| Read |  | 12 | Boiler1 | isInMaintenance |  |  |  |  | bit
INPUT_REGISTER | Read | 8014 |  | Boiler1 | Request Working Mode |  |  | 0-Off 1-Take_Heat 2-Give_Heat |  | int
INPUT_REGISTER | Read | 8015 |  | Boiler1 | Request Temperature Setpoint |  |  |  | °C | int
INPUT_REGISTER | Read | 8016 |  | Boiler1 | Request Power Setpoint |  |  |  | % | int
INPUT_REGISTER | Read | 8017 |  | Boiler1 | Current Pressure |  |  |  | bar | signed int | x10
INPUT_REGISTER | Read | 8018 |  | Boiler1 | Error Cause Code |  |  |  |  | int
INPUT_REGISTER | Read | 8019 |  | Boiler1 | Error Display Code |  |  |  |  | int
INPUT_REGISTER | Read | 8020 |  | Boiler1 | Cascade Start Index | 1 | 16 |  |  | int
INPUT_REGISTER | Read | 8021 |  | Boiler1 | Number of Starts |  |  |  |  | long
INPUT_REGISTER | Read | 8023 |  | Boiler1 | Operating Time |  |  |  | min | long
INPUT_REGISTER | Read | 8025 |  | Boiler1 | Valve Position |  |  |  | % | int
INPUT_REGISTER | Read | 8026 |  | Boiler1 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 8027 |  | Boiler1 | Stb temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 8040 |  | Boiler2 | Boiler Type |  |  | 0-None 1-EMS 2-SAFe 3-SEVEN_POLE 4-SLAVE_CBC |  | int
INPUT_REGISTER | Read | 8041 |  | Boiler2 | Flow temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 8042 |  | Boiler2 | Flow temperature rate of change |  |  |  | K/min | signed int | x10
INPUT_REGISTER | Read | 8043 |  | Boiler2 | Return Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 8044 |  | Boiler2 | Current power |  |  |  | % | int
INPUT_REGISTER | Read | 8045 |  | Boiler2 | Load limit continuous |  |  |  | % | int
INPUT_REGISTER | Read | 8046 |  | Boiler2 | Operating temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 8047 |  | Boiler2 | Maximum power |  |  |  | kW | int
INPUT_REGISTER | Read | 8048 |  | Boiler2 | Minimum relative power |  |  |  | % | int
INPUT_REGISTER | Read | 8049 |  | Boiler2 | Burner type |  |  | 0-Modulating 1-One_Stage 2-Two_Stage |  | int
INPUT_REGISTER | Read | 8050 |  | Boiler2 | Fuel type |  |  | 0-Gas 1-Oil |  | int
INPUT_REGISTER | Read | 8051 |  | Boiler2 | Maximum Temp Setpoint |  |  |  | °C | int
INPUT_REGISTER | Read | 8052 |  | Boiler2 | Hmi State |  |  | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 8053 |  | Boiler2 | bitblock |  |  |  |  | int
| Read |  | 0 | Boiler2 | isControlPossible |  |  |  |  | bit
| Read |  | 1 | Boiler2 | isForcedFlow |  |  |  |  | bit
| Read |  | 2 | Boiler2 | isTakeHeat |  |  |  |  | bit
| Read |  | 3 | Boiler2 | isLoadLimitDigital |  |  |  |  | bit
| Read |  | 4 | Boiler2 | isLoadLimitFastReduction |  |  |  |  | bit
| Read |  | 5 | Boiler2 | isBurnerOn |  |  |  |  | bit
| Read |  | 6 | Boiler2 | isRequestLeading |  |  |  |  | bit
| Read |  | 7 | Boiler2 | isRequestPriority |  |  |  |  | bit
| Read |  | 8 | Boiler2 | isRequestFlowControl |  |  |  |  | bit
| Read |  | 9 | Boiler2 | isRequestPowerControl |  |  |  |  | bit
| Read |  | 10 | Boiler2 | isLocked |  |  |  |  | bit
| Read |  | 11 | Boiler2 | isBlocked |  |  |  |  | bit
| Read |  | 12 | Boiler2 | isInMaintenance |  |  |  |  | bit
INPUT_REGISTER | Read | 8054 |  | Boiler2 | Request Working Mode |  |  | 0-Off 1-Take_Heat 2-Give_Heat |  | int
INPUT_REGISTER | Read | 8055 |  | Boiler2 | Request Temperature Setpoint |  |  |  | °C | int
INPUT_REGISTER | Read | 8056 |  | Boiler2 | Request Power Setpoint |  |  |  | % | int
INPUT_REGISTER | Read | 8057 |  | Boiler2 | Current Pressure |  |  |  | bar | signed int | x10
INPUT_REGISTER | Read | 8058 |  | Boiler2 | Error Cause Code |  |  |  |  | int
INPUT_REGISTER | Read | 8059 |  | Boiler2 | Error Display Code |  |  |  |  | int
INPUT_REGISTER | Read | 8060 |  | Boiler2 | Cascade Start Index | 1 | 16 |  |  | int
INPUT_REGISTER | Read | 8061 |  | Boiler2 | Number of Starts |  |  |  |  | long
INPUT_REGISTER | Read | 8063 |  | Boiler2 | Operating Time |  |  |  | min | long
INPUT_REGISTER | Read | 8065 |  | Boiler2 | Valve Position |  |  |  | % | int
INPUT_REGISTER | Read | 8066 |  | Boiler2 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 8067 |  | Boiler2 | Stb temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 8080 |  | Boiler3 | Boiler Type |  |  | 0-None 1-EMS 2-SAFe 3-SEVEN_POLE 4-SLAVE_CBC |  | int
INPUT_REGISTER | Read | 8081 |  | Boiler3 | Flow temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 8082 |  | Boiler3 | Flow temperature rate of change |  |  |  | K/min | signed int | x10
INPUT_REGISTER | Read | 8083 |  | Boiler3 | Return Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 8084 |  | Boiler3 | Current power |  |  |  | % | int
INPUT_REGISTER | Read | 8085 |  | Boiler3 | Load limit continuous |  |  |  | % | int
INPUT_REGISTER | Read | 8086 |  | Boiler3 | Operating temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 8087 |  | Boiler3 | Maximum power |  |  |  | kW | int
INPUT_REGISTER | Read | 8088 |  | Boiler3 | Minimum relative power |  |  |  | % | int
INPUT_REGISTER | Read | 8089 |  | Boiler3 | Burner type |  |  | 0-Modulating 1-One_Stage 2-Two_Stage |  | int
INPUT_REGISTER | Read | 8090 |  | Boiler3 | Fuel type |  |  | 0-Gas 1-Oil |  | int
INPUT_REGISTER | Read | 8091 |  | Boiler3 | Maximum Temp Setpoint |  |  |  | °C | int
INPUT_REGISTER | Read | 8092 |  | Boiler3 | Hmi State |  |  | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 8093 |  | Boiler3 | bitblock |  |  |  |  | int
| Read |  | 0 | Boiler3 | isControlPossible |  |  |  |  | bit
| Read |  | 1 | Boiler3 | isForcedFlow |  |  |  |  | bit
| Read |  | 2 | Boiler3 | isTakeHeat |  |  |  |  | bit
| Read |  | 3 | Boiler3 | isLoadLimitDigital |  |  |  |  | bit
| Read |  | 4 | Boiler3 | isLoadLimitFastReduction |  |  |  |  | bit
| Read |  | 5 | Boiler3 | isBurnerOn |  |  |  |  | bit
| Read |  | 6 | Boiler3 | isRequestLeading |  |  |  |  | bit
| Read |  | 7 | Boiler3 | isRequestPriority |  |  |  |  | bit
| Read |  | 8 | Boiler3 | isRequestFlowControl |  |  |  |  | bit
| Read |  | 9 | Boiler3 | isRequestPowerControl |  |  |  |  | bit
| Read |  | 10 | Boiler3 | isLocked |  |  |  |  | bit
| Read |  | 11 | Boiler3 | isBlocked |  |  |  |  | bit
| Read |  | 12 | Boiler3 | isInMaintenance |  |  |  |  | bit
INPUT_REGISTER | Read | 8094 |  | Boiler3 | Request Working Mode |  |  | 0-Off 1-Take_Heat 2-Give_Heat |  | int
INPUT_REGISTER | Read | 8095 |  | Boiler3 | Request Temperature Setpoint |  |  |  | °C | int
INPUT_REGISTER | Read | 8096 |  | Boiler3 | Request Power Setpoint |  |  |  | % | int
INPUT_REGISTER | Read | 8097 |  | Boiler3 | Current Pressure |  |  |  | bar | signed int | x10
INPUT_REGISTER | Read | 8098 |  | Boiler3 | Error Cause Code |  |  |  |  | int
INPUT_REGISTER | Read | 8099 |  | Boiler3 | Error Display Code |  |  |  |  | int
INPUT_REGISTER | Read | 8100 |  | Boiler3 | Cascade Start Index | 1 | 16 |  |  | int
INPUT_REGISTER | Read | 8101 |  | Boiler3 | Number of Starts |  |  |  |  | long
INPUT_REGISTER | Read | 8103 |  | Boiler3 | Operating Time |  |  |  | min | long
INPUT_REGISTER | Read | 8105 |  | Boiler3 | Valve Position |  |  |  | % | int
INPUT_REGISTER | Read | 8106 |  | Boiler3 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 8107 |  | Boiler3 | Stb temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 8120 |  | Boiler4 | Boiler Type |  |  | 0-None 1-EMS 2-SAFe 3-SEVEN_POLE 4-SLAVE_CBC |  | int
INPUT_REGISTER | Read | 8121 |  | Boiler4 | Flow temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 8122 |  | Boiler4 | Flow temperature rate of change |  |  |  | K/min | signed int | x10
INPUT_REGISTER | Read | 8123 |  | Boiler4 | Return Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 8124 |  | Boiler4 | Current power |  |  |  | % | int
INPUT_REGISTER | Read | 8125 |  | Boiler4 | Load limit continuous |  |  |  | % | int
INPUT_REGISTER | Read | 8126 |  | Boiler4 | Operating temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 8127 |  | Boiler4 | Maximum power |  |  |  | kW | int
INPUT_REGISTER | Read | 8128 |  | Boiler4 | Minimum relative power |  |  |  | % | int
INPUT_REGISTER | Read | 8129 |  | Boiler4 | Burner type |  |  | 0-Modulating 1-One_Stage 2-Two_Stage |  | int
INPUT_REGISTER | Read | 8130 |  | Boiler4 | Fuel type |  |  | 0-Gas 1-Oil |  | int
INPUT_REGISTER | Read | 8131 |  | Boiler4 | Maximum Temp Setpoint |  |  |  | °C | int
INPUT_REGISTER | Read | 8132 |  | Boiler4 | Hmi State |  |  | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 8133 |  | Boiler4 | bitblock |  |  |  |  | int
| Read |  | 0 | Boiler4 | isControlPossible |  |  |  |  | bit
| Read |  | 1 | Boiler4 | isForcedFlow |  |  |  |  | bit
| Read |  | 2 | Boiler4 | isTakeHeat |  |  |  |  | bit
| Read |  | 3 | Boiler4 | isLoadLimitDigital |  |  |  |  | bit
| Read |  | 4 | Boiler4 | isLoadLimitFastReduction |  |  |  |  | bit
| Read |  | 5 | Boiler4 | isBurnerOn |  |  |  |  | bit
| Read |  | 6 | Boiler4 | isRequestLeading |  |  |  |  | bit
| Read |  | 7 | Boiler4 | isRequestPriority |  |  |  |  | bit
| Read |  | 8 | Boiler4 | isRequestFlowControl |  |  |  |  | bit
| Read |  | 9 | Boiler4 | isRequestPowerControl |  |  |  |  | bit
| Read |  | 10 | Boiler4 | isLocked |  |  |  |  | bit
| Read |  | 11 | Boiler4 | isBlocked |  |  |  |  | bit
| Read |  | 12 | Boiler4 | isInMaintenance |  |  |  |  | bit
INPUT_REGISTER | Read | 8134 |  | Boiler4 | Request Working Mode |  |  | 0-Off 1-Take_Heat 2-Give_Heat |  | int
INPUT_REGISTER | Read | 8135 |  | Boiler4 | Request Temperature Setpoint |  |  |  | °C | int
INPUT_REGISTER | Read | 8136 |  | Boiler4 | Request Power Setpoint |  |  |  | % | int
INPUT_REGISTER | Read | 8137 |  | Boiler4 | Current Pressure |  |  |  | bar | signed int | x10
INPUT_REGISTER | Read | 8138 |  | Boiler4 | Error Cause Code |  |  |  |  | int
INPUT_REGISTER | Read | 8139 |  | Boiler4 | Error Display Code |  |  |  |  | int
INPUT_REGISTER | Read | 8140 |  | Boiler4 | Cascade Start Index | 1 | 16 |  |  | int
INPUT_REGISTER | Read | 8141 |  | Boiler4 | Number of Starts |  |  |  |  | long
INPUT_REGISTER | Read | 8143 |  | Boiler4 | Operating Time |  |  |  | min | long
INPUT_REGISTER | Read | 8145 |  | Boiler4 | Valve Position |  |  |  | % | int
INPUT_REGISTER | Read | 8146 |  | Boiler4 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 8147 |  | Boiler4 | Stb temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 8160 |  | Boiler5 | Boiler Type |  |  | 0-None 1-EMS 2-SAFe 3-SEVEN_POLE 4-SLAVE_CBC |  | int
INPUT_REGISTER | Read | 8161 |  | Boiler5 | Flow temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 8162 |  | Boiler5 | Flow temperature rate of change |  |  |  | K/min | signed int | x10
INPUT_REGISTER | Read | 8163 |  | Boiler5 | Return Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 8164 |  | Boiler5 | Current power |  |  |  | % | int
INPUT_REGISTER | Read | 8165 |  | Boiler5 | Load limit continuous |  |  |  | % | int
INPUT_REGISTER | Read | 8166 |  | Boiler5 | Operating temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 8167 |  | Boiler5 | Maximum power |  |  |  | kW | int
INPUT_REGISTER | Read | 8168 |  | Boiler5 | Minimum relative power |  |  |  | % | int
INPUT_REGISTER | Read | 8169 |  | Boiler5 | Burner type |  |  | 0-Modulating 1-One_Stage 2-Two_Stage |  | int
INPUT_REGISTER | Read | 8170 |  | Boiler5 | Fuel type |  |  | 0-Gas 1-Oil |  | int
INPUT_REGISTER | Read | 8171 |  | Boiler5 | Maximum Temp Setpoint |  |  |  | °C | int
INPUT_REGISTER | Read | 8172 |  | Boiler5 | Hmi State |  |  | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 8173 |  | Boiler5 | bitblock |  |  |  |  | int
| Read |  | 0 | Boiler5 | isControlPossible |  |  |  |  | bit
| Read |  | 1 | Boiler5 | isForcedFlow |  |  |  |  | bit
| Read |  | 2 | Boiler5 | isTakeHeat |  |  |  |  | bit
| Read |  | 3 | Boiler5 | isLoadLimitDigital |  |  |  |  | bit
| Read |  | 4 | Boiler5 | isLoadLimitFastReduction |  |  |  |  | bit
| Read |  | 5 | Boiler5 | isBurnerOn |  |  |  |  | bit
| Read |  | 6 | Boiler5 | isRequestLeading |  |  |  |  | bit
| Read |  | 7 | Boiler5 | isRequestPriority |  |  |  |  | bit
| Read |  | 8 | Boiler5 | isRequestFlowControl |  |  |  |  | bit
| Read |  | 9 | Boiler5 | isRequestPowerControl |  |  |  |  | bit
| Read |  | 10 | Boiler5 | isLocked |  |  |  |  | bit
| Read |  | 11 | Boiler5 | isBlocked |  |  |  |  | bit
| Read |  | 12 | Boiler5 | isInMaintenance |  |  |  |  | bit
INPUT_REGISTER | Read | 8174 |  | Boiler5 | Request Working Mode |  |  | 0-Off 1-Take_Heat 2-Give_Heat |  | int
INPUT_REGISTER | Read | 8175 |  | Boiler5 | Request Temperature Setpoint |  |  |  | °C | int
INPUT_REGISTER | Read | 8176 |  | Boiler5 | Request Power Setpoint |  |  |  | % | int
INPUT_REGISTER | Read | 8177 |  | Boiler5 | Current Pressure |  |  |  | bar | signed int | x10
INPUT_REGISTER | Read | 8178 |  | Boiler5 | Error Cause Code |  |  |  |  | int
INPUT_REGISTER | Read | 8179 |  | Boiler5 | Error Display Code |  |  |  |  | int
INPUT_REGISTER | Read | 8180 |  | Boiler5 | Cascade Start Index | 1 | 16 |  |  | int
INPUT_REGISTER | Read | 8181 |  | Boiler5 | Number of Starts |  |  |  |  | long
INPUT_REGISTER | Read | 8183 |  | Boiler5 | Operating Time |  |  |  | min | long
INPUT_REGISTER | Read | 8185 |  | Boiler5 | Valve Position |  |  |  | % | int
INPUT_REGISTER | Read | 8186 |  | Boiler5 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 8187 |  | Boiler5 | Stb temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 8200 |  | Boiler6 | Boiler Type |  |  | 0-None 1-EMS 2-SAFe 3-SEVEN_POLE 4-SLAVE_CBC |  | int
INPUT_REGISTER | Read | 8201 |  | Boiler6 | Flow temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 8202 |  | Boiler6 | Flow temperature rate of change |  |  |  | K/min | signed int | x10
INPUT_REGISTER | Read | 8203 |  | Boiler6 | Return Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 8204 |  | Boiler6 | Current power |  |  |  | % | int
INPUT_REGISTER | Read | 8205 |  | Boiler6 | Load limit continuous |  |  |  | % | int
INPUT_REGISTER | Read | 8206 |  | Boiler6 | Operating temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 8207 |  | Boiler6 | Maximum power |  |  |  | kW | int
INPUT_REGISTER | Read | 8208 |  | Boiler6 | Minimum relative power |  |  |  | % | int
INPUT_REGISTER | Read | 8209 |  | Boiler6 | Burner type |  |  | 0-Modulating 1-One_Stage 2-Two_Stage |  | int
INPUT_REGISTER | Read | 8210 |  | Boiler6 | Fuel type |  |  | 0-Gas 1-Oil |  | int
INPUT_REGISTER | Read | 8211 |  | Boiler6 | Maximum Temp Setpoint |  |  |  | °C | int
INPUT_REGISTER | Read | 8212 |  | Boiler6 | Hmi State |  |  | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 8213 |  | Boiler6 | bitblock |  |  |  |  | int
| Read |  | 0 | Boiler6 | isControlPossible |  |  |  |  | bit
| Read |  | 1 | Boiler6 | isForcedFlow |  |  |  |  | bit
| Read |  | 2 | Boiler6 | isTakeHeat |  |  |  |  | bit
| Read |  | 3 | Boiler6 | isLoadLimitDigital |  |  |  |  | bit
| Read |  | 4 | Boiler6 | isLoadLimitFastReduction |  |  |  |  | bit
| Read |  | 5 | Boiler6 | isBurnerOn |  |  |  |  | bit
| Read |  | 6 | Boiler6 | isRequestLeading |  |  |  |  | bit
| Read |  | 7 | Boiler6 | isRequestPriority |  |  |  |  | bit
| Read |  | 8 | Boiler6 | isRequestFlowControl |  |  |  |  | bit
| Read |  | 9 | Boiler6 | isRequestPowerControl |  |  |  |  | bit
| Read |  | 10 | Boiler6 | isLocked |  |  |  |  | bit
| Read |  | 11 | Boiler6 | isBlocked |  |  |  |  | bit
| Read |  | 12 | Boiler6 | isInMaintenance |  |  |  |  | bit
INPUT_REGISTER | Read | 8214 |  | Boiler6 | Request Working Mode |  |  | 0-Off 1-Take_Heat 2-Give_Heat |  | int
INPUT_REGISTER | Read | 8215 |  | Boiler6 | Request Temperature Setpoint |  |  |  | °C | int
INPUT_REGISTER | Read | 8216 |  | Boiler6 | Request Power Setpoint |  |  |  | % | int
INPUT_REGISTER | Read | 8217 |  | Boiler6 | Current Pressure |  |  |  | bar | signed int | x10
INPUT_REGISTER | Read | 8218 |  | Boiler6 | Error Cause Code |  |  |  |  | int
INPUT_REGISTER | Read | 8219 |  | Boiler6 | Error Display Code |  |  |  |  | int
INPUT_REGISTER | Read | 8220 |  | Boiler6 | Cascade Start Index | 1 | 16 |  |  | int
INPUT_REGISTER | Read | 8221 |  | Boiler6 | Number of Starts |  |  |  |  | long
INPUT_REGISTER | Read | 8223 |  | Boiler6 | Operating Time |  |  |  | min | long
INPUT_REGISTER | Read | 8225 |  | Boiler6 | Valve Position |  |  |  | % | int
INPUT_REGISTER | Read | 8226 |  | Boiler6 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 8227 |  | Boiler6 | Stb temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 8240 |  | Boiler7 | Boiler Type |  |  | 0-None 1-EMS 2-SAFe 3-SEVEN_POLE 4-SLAVE_CBC |  | int
INPUT_REGISTER | Read | 8241 |  | Boiler7 | Flow temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 8242 |  | Boiler7 | Flow temperature rate of change |  |  |  | K/min | signed int | x10
INPUT_REGISTER | Read | 8243 |  | Boiler7 | Return Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 8244 |  | Boiler7 | Current power |  |  |  | % | int
INPUT_REGISTER | Read | 8245 |  | Boiler7 | Load limit continuous |  |  |  | % | int
INPUT_REGISTER | Read | 8246 |  | Boiler7 | Operating temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 8247 |  | Boiler7 | Maximum power |  |  |  | kW | int
INPUT_REGISTER | Read | 8248 |  | Boiler7 | Minimum relative power |  |  |  | % | int
INPUT_REGISTER | Read | 8249 |  | Boiler7 | Burner type |  |  | 0-Modulating 1-One_Stage 2-Two_Stage |  | int
INPUT_REGISTER | Read | 8250 |  | Boiler7 | Fuel type |  |  | 0-Gas 1-Oil |  | int
INPUT_REGISTER | Read | 8251 |  | Boiler7 | Maximum Temp Setpoint |  |  |  | °C | int
INPUT_REGISTER | Read | 8252 |  | Boiler7 | Hmi State |  |  | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 8253 |  | Boiler7 | bitblock |  |  |  |  | int
| Read |  | 0 | Boiler7 | isControlPossible |  |  |  |  | bit
| Read |  | 1 | Boiler7 | isForcedFlow |  |  |  |  | bit
| Read |  | 2 | Boiler7 | isTakeHeat |  |  |  |  | bit
| Read |  | 3 | Boiler7 | isLoadLimitDigital |  |  |  |  | bit
| Read |  | 4 | Boiler7 | isLoadLimitFastReduction |  |  |  |  | bit
| Read |  | 5 | Boiler7 | isBurnerOn |  |  |  |  | bit
| Read |  | 6 | Boiler7 | isRequestLeading |  |  |  |  | bit
| Read |  | 7 | Boiler7 | isRequestPriority |  |  |  |  | bit
| Read |  | 8 | Boiler7 | isRequestFlowControl |  |  |  |  | bit
| Read |  | 9 | Boiler7 | isRequestPowerControl |  |  |  |  | bit
| Read |  | 10 | Boiler7 | isLocked |  |  |  |  | bit
| Read |  | 11 | Boiler7 | isBlocked |  |  |  |  | bit
| Read |  | 12 | Boiler7 | isInMaintenance |  |  |  |  | bit
INPUT_REGISTER | Read | 8254 |  | Boiler7 | Request Working Mode |  |  | 0-Off 1-Take_Heat 2-Give_Heat |  | int
INPUT_REGISTER | Read | 8255 |  | Boiler7 | Request Temperature Setpoint |  |  |  | °C | int
INPUT_REGISTER | Read | 8256 |  | Boiler7 | Request Power Setpoint |  |  |  | % | int
INPUT_REGISTER | Read | 8257 |  | Boiler7 | Current Pressure |  |  |  | bar | signed int | x10
INPUT_REGISTER | Read | 8258 |  | Boiler7 | Error Cause Code |  |  |  |  | int
INPUT_REGISTER | Read | 8259 |  | Boiler7 | Error Display Code |  |  |  |  | int
INPUT_REGISTER | Read | 8260 |  | Boiler7 | Cascade Start Index | 1 | 16 |  |  | int
INPUT_REGISTER | Read | 8261 |  | Boiler7 | Number of Starts |  |  |  |  | long
INPUT_REGISTER | Read | 8263 |  | Boiler7 | Operating Time |  |  |  | min | long
INPUT_REGISTER | Read | 8265 |  | Boiler7 | Valve Position |  |  |  | % | int
INPUT_REGISTER | Read | 8266 |  | Boiler7 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 8267 |  | Boiler7 | Stb temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 8280 |  | Boiler8 | Boiler Type |  |  | 0-None 1-EMS 2-SAFe 3-SEVEN_POLE 4-SLAVE_CBC |  | int
INPUT_REGISTER | Read | 8281 |  | Boiler8 | Flow temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 8282 |  | Boiler8 | Flow temperature rate of change |  |  |  | K/min | signed int | x10
INPUT_REGISTER | Read | 8283 |  | Boiler8 | Return Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 8284 |  | Boiler8 | Current power |  |  |  | % | int
INPUT_REGISTER | Read | 8285 |  | Boiler8 | Load limit continuous |  |  |  | % | int
INPUT_REGISTER | Read | 8286 |  | Boiler8 | Operating temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 8287 |  | Boiler8 | Maximum power |  |  |  | kW | int
INPUT_REGISTER | Read | 8288 |  | Boiler8 | Minimum relative power |  |  |  | % | int
INPUT_REGISTER | Read | 8289 |  | Boiler8 | Burner type |  |  | 0-Modulating 1-One_Stage 2-Two_Stage |  | int
INPUT_REGISTER | Read | 8290 |  | Boiler8 | Fuel type |  |  | 0-Gas 1-Oil |  | int
INPUT_REGISTER | Read | 8291 |  | Boiler8 | Maximum Temp Setpoint |  |  |  | °C | int
INPUT_REGISTER | Read | 8292 |  | Boiler8 | Hmi State |  |  | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 8293 |  | Boiler8 | bitblock |  |  |  |  | int
| Read |  | 0 | Boiler8 | isControlPossible |  |  |  |  | bit
| Read |  | 1 | Boiler8 | isForcedFlow |  |  |  |  | bit
| Read |  | 2 | Boiler8 | isTakeHeat |  |  |  |  | bit
| Read |  | 3 | Boiler8 | isLoadLimitDigital |  |  |  |  | bit
| Read |  | 4 | Boiler8 | isLoadLimitFastReduction |  |  |  |  | bit
| Read |  | 5 | Boiler8 | isBurnerOn |  |  |  |  | bit
| Read |  | 6 | Boiler8 | isRequestLeading |  |  |  |  | bit
| Read |  | 7 | Boiler8 | isRequestPriority |  |  |  |  | bit
| Read |  | 8 | Boiler8 | isRequestFlowControl |  |  |  |  | bit
| Read |  | 9 | Boiler8 | isRequestPowerControl |  |  |  |  | bit
| Read |  | 10 | Boiler8 | isLocked |  |  |  |  | bit
| Read |  | 11 | Boiler8 | isBlocked |  |  |  |  | bit
| Read |  | 12 | Boiler8 | isInMaintenance |  |  |  |  | bit
INPUT_REGISTER | Read | 8294 |  | Boiler8 | Request Working Mode |  |  | 0-Off 1-Take_Heat 2-Give_Heat |  | int
INPUT_REGISTER | Read | 8295 |  | Boiler8 | Request Temperature Setpoint |  |  |  | °C | int
INPUT_REGISTER | Read | 8296 |  | Boiler8 | Request Power Setpoint |  |  |  | % | int
INPUT_REGISTER | Read | 8297 |  | Boiler8 | Current Pressure |  |  |  | bar | signed int | x10
INPUT_REGISTER | Read | 8298 |  | Boiler8 | Error Cause Code |  |  |  |  | int
INPUT_REGISTER | Read | 8299 |  | Boiler8 | Error Display Code |  |  |  |  | int
INPUT_REGISTER | Read | 8300 |  | Boiler8 | Cascade Start Index | 1 | 16 |  |  | int
INPUT_REGISTER | Read | 8301 |  | Boiler8 | Number of Starts |  |  |  |  | long
INPUT_REGISTER | Read | 8303 |  | Boiler8 | Operating Time |  |  |  | min | long
INPUT_REGISTER | Read | 8305 |  | Boiler8 | Valve Position |  |  |  | % | int
INPUT_REGISTER | Read | 8306 |  | Boiler8 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 8307 |  | Boiler8 | Stb temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 8320 |  | Boiler9 | Boiler Type |  |  | 0-None 1-EMS 2-SAFe 3-SEVEN_POLE 4-SLAVE_CBC |  | int
INPUT_REGISTER | Read | 8321 |  | Boiler9 | Flow temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 8322 |  | Boiler9 | Flow temperature rate of change |  |  |  | K/min | signed int | x10
INPUT_REGISTER | Read | 8323 |  | Boiler9 | Return Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 8324 |  | Boiler9 | Current power |  |  |  | % | int
INPUT_REGISTER | Read | 8325 |  | Boiler9 | Load limit continuous |  |  |  | % | int
INPUT_REGISTER | Read | 8326 |  | Boiler9 | Operating temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 8327 |  | Boiler9 | Maximum power |  |  |  | kW | int
INPUT_REGISTER | Read | 8328 |  | Boiler9 | Minimum relative power |  |  |  | % | int
INPUT_REGISTER | Read | 8329 |  | Boiler9 | Burner type |  |  | 0-Modulating 1-One_Stage 2-Two_Stage |  | int
INPUT_REGISTER | Read | 8330 |  | Boiler9 | Fuel type |  |  | 0-Gas 1-Oil |  | int
INPUT_REGISTER | Read | 8331 |  | Boiler9 | Maximum Temp Setpoint |  |  |  | °C | int
INPUT_REGISTER | Read | 8332 |  | Boiler9 | Hmi State |  |  | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 8333 |  | Boiler9 | bitblock |  |  |  |  | int
| Read |  | 0 | Boiler9 | isControlPossible |  |  |  |  | bit
| Read |  | 1 | Boiler9 | isForcedFlow |  |  |  |  | bit
| Read |  | 2 | Boiler9 | isTakeHeat |  |  |  |  | bit
| Read |  | 3 | Boiler9 | isLoadLimitDigital |  |  |  |  | bit
| Read |  | 4 | Boiler9 | isLoadLimitFastReduction |  |  |  |  | bit
| Read |  | 5 | Boiler9 | isBurnerOn |  |  |  |  | bit
| Read |  | 6 | Boiler9 | isRequestLeading |  |  |  |  | bit
| Read |  | 7 | Boiler9 | isRequestPriority |  |  |  |  | bit
| Read |  | 8 | Boiler9 | isRequestFlowControl |  |  |  |  | bit
| Read |  | 9 | Boiler9 | isRequestPowerControl |  |  |  |  | bit
| Read |  | 10 | Boiler9 | isLocked |  |  |  |  | bit
| Read |  | 11 | Boiler9 | isBlocked |  |  |  |  | bit
| Read |  | 12 | Boiler9 | isInMaintenance |  |  |  |  | bit
INPUT_REGISTER | Read | 8334 |  | Boiler9 | Request Working Mode |  |  | 0-Off 1-Take_Heat 2-Give_Heat |  | int
INPUT_REGISTER | Read | 8335 |  | Boiler9 | Request Temperature Setpoint |  |  |  | °C | int
INPUT_REGISTER | Read | 8336 |  | Boiler9 | Request Power Setpoint |  |  |  | % | int
INPUT_REGISTER | Read | 8337 |  | Boiler9 | Current Pressure |  |  |  | bar | signed int | x10
INPUT_REGISTER | Read | 8338 |  | Boiler9 | Error Cause Code |  |  |  |  | int
INPUT_REGISTER | Read | 8339 |  | Boiler9 | Error Display Code |  |  |  |  | int
INPUT_REGISTER | Read | 8340 |  | Boiler9 | Cascade Start Index | 1 | 16 |  |  | int
INPUT_REGISTER | Read | 8341 |  | Boiler9 | Number of Starts |  |  |  |  | long
INPUT_REGISTER | Read | 8343 |  | Boiler9 | Operating Time |  |  |  | min | long
INPUT_REGISTER | Read | 8345 |  | Boiler9 | Valve Position |  |  |  | % | int
INPUT_REGISTER | Read | 8346 |  | Boiler9 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 8347 |  | Boiler9 | Stb temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 8360 |  | Boiler10 | Boiler Type |  |  | 0-None 1-EMS 2-SAFe 3-SEVEN_POLE 4-SLAVE_CBC |  | int
INPUT_REGISTER | Read | 8361 |  | Boiler10 | Flow temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 8362 |  | Boiler10 | Flow temperature rate of change |  |  |  | K/min | signed int | x10
INPUT_REGISTER | Read | 8363 |  | Boiler10 | Return Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 8364 |  | Boiler10 | Current power |  |  |  | % | int
INPUT_REGISTER | Read | 8365 |  | Boiler10 | Load limit continuous |  |  |  | % | int
INPUT_REGISTER | Read | 8366 |  | Boiler10 | Operating temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 8367 |  | Boiler10 | Maximum power |  |  |  | kW | int
INPUT_REGISTER | Read | 8368 |  | Boiler10 | Minimum relative power |  |  |  | % | int
INPUT_REGISTER | Read | 8369 |  | Boiler10 | Burner type |  |  | 0-Modulating 1-One_Stage 2-Two_Stage |  | int
INPUT_REGISTER | Read | 8370 |  | Boiler10 | Fuel type |  |  | 0-Gas 1-Oil |  | int
INPUT_REGISTER | Read | 8371 |  | Boiler10 | Maximum Temp Setpoint |  |  |  | °C | int
INPUT_REGISTER | Read | 8372 |  | Boiler10 | Hmi State |  |  | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 8373 |  | Boiler10 | bitblock |  |  |  |  | int
| Read |  | 0 | Boiler10 | isControlPossible |  |  |  |  | bit
| Read |  | 1 | Boiler10 | isForcedFlow |  |  |  |  | bit
| Read |  | 2 | Boiler10 | isTakeHeat |  |  |  |  | bit
| Read |  | 3 | Boiler10 | isLoadLimitDigital |  |  |  |  | bit
| Read |  | 4 | Boiler10 | isLoadLimitFastReduction |  |  |  |  | bit
| Read |  | 5 | Boiler10 | isBurnerOn |  |  |  |  | bit
| Read |  | 6 | Boiler10 | isRequestLeading |  |  |  |  | bit
| Read |  | 7 | Boiler10 | isRequestPriority |  |  |  |  | bit
| Read |  | 8 | Boiler10 | isRequestFlowControl |  |  |  |  | bit
| Read |  | 9 | Boiler10 | isRequestPowerControl |  |  |  |  | bit
| Read |  | 10 | Boiler10 | isLocked |  |  |  |  | bit
| Read |  | 11 | Boiler10 | isBlocked |  |  |  |  | bit
| Read |  | 12 | Boiler10 | isInMaintenance |  |  |  |  | bit
INPUT_REGISTER | Read | 8374 |  | Boiler10 | Request Working Mode |  |  | 0-Off 1-Take_Heat 2-Give_Heat |  | int
INPUT_REGISTER | Read | 8375 |  | Boiler10 | Request Temperature Setpoint |  |  |  | °C | int
INPUT_REGISTER | Read | 8376 |  | Boiler10 | Request Power Setpoint |  |  |  | % | int
INPUT_REGISTER | Read | 8377 |  | Boiler10 | Current Pressure |  |  |  | bar | signed int | x10
INPUT_REGISTER | Read | 8378 |  | Boiler10 | Error Cause Code |  |  |  |  | int
INPUT_REGISTER | Read | 8379 |  | Boiler10 | Error Display Code |  |  |  |  | int
INPUT_REGISTER | Read | 8380 |  | Boiler10 | Cascade Start Index | 1 | 16 |  |  | int
INPUT_REGISTER | Read | 8381 |  | Boiler10 | Number of Starts |  |  |  |  | long
INPUT_REGISTER | Read | 8383 |  | Boiler10 | Operating Time |  |  |  | min | long
INPUT_REGISTER | Read | 8385 |  | Boiler10 | Valve Position |  |  |  | % | int
INPUT_REGISTER | Read | 8386 |  | Boiler10 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 8387 |  | Boiler10 | Stb temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 8400 |  | Boiler11 | Boiler Type |  |  | 0-None 1-EMS 2-SAFe 3-SEVEN_POLE 4-SLAVE_CBC |  | int
INPUT_REGISTER | Read | 8401 |  | Boiler11 | Flow temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 8402 |  | Boiler11 | Flow temperature rate of change |  |  |  | K/min | signed int | x10
INPUT_REGISTER | Read | 8403 |  | Boiler11 | Return Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 8404 |  | Boiler11 | Current power |  |  |  | % | int
INPUT_REGISTER | Read | 8405 |  | Boiler11 | Load limit continuous |  |  |  | % | int
INPUT_REGISTER | Read | 8406 |  | Boiler11 | Operating temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 8407 |  | Boiler11 | Maximum power |  |  |  | kW | int
INPUT_REGISTER | Read | 8408 |  | Boiler11 | Minimum relative power |  |  |  | % | int
INPUT_REGISTER | Read | 8409 |  | Boiler11 | Burner type |  |  | 0-Modulating 1-One_Stage 2-Two_Stage |  | int
INPUT_REGISTER | Read | 8410 |  | Boiler11 | Fuel type |  |  | 0-Gas 1-Oil |  | int
INPUT_REGISTER | Read | 8411 |  | Boiler11 | Maximum Temp Setpoint |  |  |  | °C | int
INPUT_REGISTER | Read | 8412 |  | Boiler11 | Hmi State |  |  | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 8413 |  | Boiler11 | bitblock |  |  |  |  | int
| Read |  | 0 | Boiler11 | isControlPossible |  |  |  |  | bit
| Read |  | 1 | Boiler11 | isForcedFlow |  |  |  |  | bit
| Read |  | 2 | Boiler11 | isTakeHeat |  |  |  |  | bit
| Read |  | 3 | Boiler11 | isLoadLimitDigital |  |  |  |  | bit
| Read |  | 4 | Boiler11 | isLoadLimitFastReduction |  |  |  |  | bit
| Read |  | 5 | Boiler11 | isBurnerOn |  |  |  |  | bit
| Read |  | 6 | Boiler11 | isRequestLeading |  |  |  |  | bit
| Read |  | 7 | Boiler11 | isRequestPriority |  |  |  |  | bit
| Read |  | 8 | Boiler11 | isRequestFlowControl |  |  |  |  | bit
| Read |  | 9 | Boiler11 | isRequestPowerControl |  |  |  |  | bit
| Read |  | 10 | Boiler11 | isLocked |  |  |  |  | bit
| Read |  | 11 | Boiler11 | isBlocked |  |  |  |  | bit
| Read |  | 12 | Boiler11 | isInMaintenance |  |  |  |  | bit
INPUT_REGISTER | Read | 8414 |  | Boiler11 | Request Working Mode |  |  | 0-Off 1-Take_Heat 2-Give_Heat |  | int
INPUT_REGISTER | Read | 8415 |  | Boiler11 | Request Temperature Setpoint |  |  |  | °C | int
INPUT_REGISTER | Read | 8416 |  | Boiler11 | Request Power Setpoint |  |  |  | % | int
INPUT_REGISTER | Read | 8417 |  | Boiler11 | Current Pressure |  |  |  | bar | signed int | x10
INPUT_REGISTER | Read | 8418 |  | Boiler11 | Error Cause Code |  |  |  |  | int
INPUT_REGISTER | Read | 8419 |  | Boiler11 | Error Display Code |  |  |  |  | int
INPUT_REGISTER | Read | 8420 |  | Boiler11 | Cascade Start Index | 1 | 16 |  |  | int
INPUT_REGISTER | Read | 8421 |  | Boiler11 | Number of Starts |  |  |  |  | long
INPUT_REGISTER | Read | 8423 |  | Boiler11 | Operating Time |  |  |  | min | long
INPUT_REGISTER | Read | 8425 |  | Boiler11 | Valve Position |  |  |  | % | int
INPUT_REGISTER | Read | 8426 |  | Boiler11 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 8427 |  | Boiler11 | Stb temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 8440 |  | Boiler12 | Boiler Type |  |  | 0-None 1-EMS 2-SAFe 3-SEVEN_POLE 4-SLAVE_CBC |  | int
INPUT_REGISTER | Read | 8441 |  | Boiler12 | Flow temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 8442 |  | Boiler12 | Flow temperature rate of change |  |  |  | K/min | signed int | x10
INPUT_REGISTER | Read | 8443 |  | Boiler12 | Return Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 8444 |  | Boiler12 | Current power |  |  |  | % | int
INPUT_REGISTER | Read | 8445 |  | Boiler12 | Load limit continuous |  |  |  | % | int
INPUT_REGISTER | Read | 8446 |  | Boiler12 | Operating temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 8447 |  | Boiler12 | Maximum power |  |  |  | kW | int
INPUT_REGISTER | Read | 8448 |  | Boiler12 | Minimum relative power |  |  |  | % | int
INPUT_REGISTER | Read | 8449 |  | Boiler12 | Burner type |  |  | 0-Modulating 1-One_Stage 2-Two_Stage |  | int
INPUT_REGISTER | Read | 8450 |  | Boiler12 | Fuel type |  |  | 0-Gas 1-Oil |  | int
INPUT_REGISTER | Read | 8451 |  | Boiler12 | Maximum Temp Setpoint |  |  |  | °C | int
INPUT_REGISTER | Read | 8452 |  | Boiler12 | Hmi State |  |  | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 8453 |  | Boiler12 | bitblock |  |  |  |  | int
| Read |  | 0 | Boiler12 | isControlPossible |  |  |  |  | bit
| Read |  | 1 | Boiler12 | isForcedFlow |  |  |  |  | bit
| Read |  | 2 | Boiler12 | isTakeHeat |  |  |  |  | bit
| Read |  | 3 | Boiler12 | isLoadLimitDigital |  |  |  |  | bit
| Read |  | 4 | Boiler12 | isLoadLimitFastReduction |  |  |  |  | bit
| Read |  | 5 | Boiler12 | isBurnerOn |  |  |  |  | bit
| Read |  | 6 | Boiler12 | isRequestLeading |  |  |  |  | bit
| Read |  | 7 | Boiler12 | isRequestPriority |  |  |  |  | bit
| Read |  | 8 | Boiler12 | isRequestFlowControl |  |  |  |  | bit
| Read |  | 9 | Boiler12 | isRequestPowerControl |  |  |  |  | bit
| Read |  | 10 | Boiler12 | isLocked |  |  |  |  | bit
| Read |  | 11 | Boiler12 | isBlocked |  |  |  |  | bit
| Read |  | 12 | Boiler12 | isInMaintenance |  |  |  |  | bit
INPUT_REGISTER | Read | 8454 |  | Boiler12 | Request Working Mode |  |  | 0-Off 1-Take_Heat 2-Give_Heat |  | int
INPUT_REGISTER | Read | 8455 |  | Boiler12 | Request Temperature Setpoint |  |  |  | °C | int
INPUT_REGISTER | Read | 8456 |  | Boiler12 | Request Power Setpoint |  |  |  | % | int
INPUT_REGISTER | Read | 8457 |  | Boiler12 | Current Pressure |  |  |  | bar | signed int | x10
INPUT_REGISTER | Read | 8458 |  | Boiler12 | Error Cause Code |  |  |  |  | int
INPUT_REGISTER | Read | 8459 |  | Boiler12 | Error Display Code |  |  |  |  | int
INPUT_REGISTER | Read | 8460 |  | Boiler12 | Cascade Start Index | 1 | 16 |  |  | int
INPUT_REGISTER | Read | 8461 |  | Boiler12 | Number of Starts |  |  |  |  | long
INPUT_REGISTER | Read | 8463 |  | Boiler12 | Operating Time |  |  |  | min | long
INPUT_REGISTER | Read | 8465 |  | Boiler12 | Valve Position |  |  |  | % | int
INPUT_REGISTER | Read | 8466 |  | Boiler12 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 8467 |  | Boiler12 | Stb temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 8480 |  | Boiler13 | Boiler Type |  |  | 0-None 1-EMS 2-SAFe 3-SEVEN_POLE 4-SLAVE_CBC |  | int
INPUT_REGISTER | Read | 8481 |  | Boiler13 | Flow temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 8482 |  | Boiler13 | Flow temperature rate of change |  |  |  | K/min | signed int | x10
INPUT_REGISTER | Read | 8483 |  | Boiler13 | Return Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 8484 |  | Boiler13 | Current power |  |  |  | % | int
INPUT_REGISTER | Read | 8485 |  | Boiler13 | Load limit continuous |  |  |  | % | int
INPUT_REGISTER | Read | 8486 |  | Boiler13 | Operating temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 8487 |  | Boiler13 | Maximum power |  |  |  | kW | int
INPUT_REGISTER | Read | 8488 |  | Boiler13 | Minimum relative power |  |  |  | % | int
INPUT_REGISTER | Read | 8489 |  | Boiler13 | Burner type |  |  | 0-Modulating 1-One_Stage 2-Two_Stage |  | int
INPUT_REGISTER | Read | 8490 |  | Boiler13 | Fuel type |  |  | 0-Gas 1-Oil |  | int
INPUT_REGISTER | Read | 8491 |  | Boiler13 | Maximum Temp Setpoint |  |  |  | °C | int
INPUT_REGISTER | Read | 8492 |  | Boiler13 | Hmi State |  |  | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 8493 |  | Boiler13 | bitblock |  |  |  |  | int
| Read |  | 0 | Boiler13 | isControlPossible |  |  |  |  | bit
| Read |  | 1 | Boiler13 | isForcedFlow |  |  |  |  | bit
| Read |  | 2 | Boiler13 | isTakeHeat |  |  |  |  | bit
| Read |  | 3 | Boiler13 | isLoadLimitDigital |  |  |  |  | bit
| Read |  | 4 | Boiler13 | isLoadLimitFastReduction |  |  |  |  | bit
| Read |  | 5 | Boiler13 | isBurnerOn |  |  |  |  | bit
| Read |  | 6 | Boiler13 | isRequestLeading |  |  |  |  | bit
| Read |  | 7 | Boiler13 | isRequestPriority |  |  |  |  | bit
| Read |  | 8 | Boiler13 | isRequestFlowControl |  |  |  |  | bit
| Read |  | 9 | Boiler13 | isRequestPowerControl |  |  |  |  | bit
| Read |  | 10 | Boiler13 | isLocked |  |  |  |  | bit
| Read |  | 11 | Boiler13 | isBlocked |  |  |  |  | bit
| Read |  | 12 | Boiler13 | isInMaintenance |  |  |  |  | bit
INPUT_REGISTER | Read | 8494 |  | Boiler13 | Request Working Mode |  |  | 0-Off 1-Take_Heat 2-Give_Heat |  | int
INPUT_REGISTER | Read | 8495 |  | Boiler13 | Request Temperature Setpoint |  |  |  | °C | int
INPUT_REGISTER | Read | 8496 |  | Boiler13 | Request Power Setpoint |  |  |  | % | int
INPUT_REGISTER | Read | 8497 |  | Boiler13 | Current Pressure |  |  |  | bar | signed int | x10
INPUT_REGISTER | Read | 8498 |  | Boiler13 | Error Cause Code |  |  |  |  | int
INPUT_REGISTER | Read | 8499 |  | Boiler13 | Error Display Code |  |  |  |  | int
INPUT_REGISTER | Read | 8500 |  | Boiler13 | Cascade Start Index | 1 | 16 |  |  | int
INPUT_REGISTER | Read | 8501 |  | Boiler13 | Number of Starts |  |  |  |  | long
INPUT_REGISTER | Read | 8503 |  | Boiler13 | Operating Time |  |  |  | min | long
INPUT_REGISTER | Read | 8505 |  | Boiler13 | Valve Position |  |  |  | % | int
INPUT_REGISTER | Read | 8506 |  | Boiler13 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 8507 |  | Boiler13 | Stb temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 8520 |  | Boiler14 | Boiler Type |  |  | 0-None 1-EMS 2-SAFe 3-SEVEN_POLE 4-SLAVE_CBC |  | int
INPUT_REGISTER | Read | 8521 |  | Boiler14 | Flow temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 8522 |  | Boiler14 | Flow temperature rate of change |  |  |  | K/min | signed int | x10
INPUT_REGISTER | Read | 8523 |  | Boiler14 | Return Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 8524 |  | Boiler14 | Current power |  |  |  | % | int
INPUT_REGISTER | Read | 8525 |  | Boiler14 | Load limit continuous |  |  |  | % | int
INPUT_REGISTER | Read | 8526 |  | Boiler14 | Operating temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 8527 |  | Boiler14 | Maximum power |  |  |  | kW | int
INPUT_REGISTER | Read | 8528 |  | Boiler14 | Minimum relative power |  |  |  | % | int
INPUT_REGISTER | Read | 8529 |  | Boiler14 | Burner type |  |  | 0-Modulating 1-One_Stage 2-Two_Stage |  | int
INPUT_REGISTER | Read | 8530 |  | Boiler14 | Fuel type |  |  | 0-Gas 1-Oil |  | int
INPUT_REGISTER | Read | 8531 |  | Boiler14 | Maximum Temp Setpoint |  |  |  | °C | int
INPUT_REGISTER | Read | 8532 |  | Boiler14 | Hmi State |  |  | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 8533 |  | Boiler14 | bitblock |  |  |  |  | int
| Read |  | 0 | Boiler14 | isControlPossible |  |  |  |  | bit
| Read |  | 1 | Boiler14 | isForcedFlow |  |  |  |  | bit
| Read |  | 2 | Boiler14 | isTakeHeat |  |  |  |  | bit
| Read |  | 3 | Boiler14 | isLoadLimitDigital |  |  |  |  | bit
| Read |  | 4 | Boiler14 | isLoadLimitFastReduction |  |  |  |  | bit
| Read |  | 5 | Boiler14 | isBurnerOn |  |  |  |  | bit
| Read |  | 6 | Boiler14 | isRequestLeading |  |  |  |  | bit
| Read |  | 7 | Boiler14 | isRequestPriority |  |  |  |  | bit
| Read |  | 8 | Boiler14 | isRequestFlowControl |  |  |  |  | bit
| Read |  | 9 | Boiler14 | isRequestPowerControl |  |  |  |  | bit
INPUT_REGISTER | Read | 8534 |  | Boiler14 | Request Working Mode |  |  | 0-Off 1-Take_Heat 2-Give_Heat |  | int
INPUT_REGISTER | Read | 8535 |  | Boiler14 | Request Temperature Setpoint |  |  |  | °C | int
INPUT_REGISTER | Read | 8536 |  | Boiler14 | Request Power Setpoint |  |  |  | % | int
INPUT_REGISTER | Read | 8537 |  | Boiler14 | Current Pressure |  |  |  | bar | signed int | x10
INPUT_REGISTER | Read | 8538 |  | Boiler14 | Error Cause Code |  |  |  |  | int
INPUT_REGISTER | Read | 8539 |  | Boiler14 | Error Display Code |  |  |  |  | int
INPUT_REGISTER | Read | 8540 |  | Boiler14 | Cascade Start Index | 1 | 16 |  |  | int
INPUT_REGISTER | Read | 8541 |  | Boiler14 | Number of Starts |  |  |  |  | long
INPUT_REGISTER | Read | 8543 |  | Boiler14 | Operating Time |  |  |  | min | long
INPUT_REGISTER | Read | 8545 |  | Boiler14 | Valve Position |  |  |  | % | int
INPUT_REGISTER | Read | 8546 |  | Boiler14 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 8547 |  | Boiler14 | Stb temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 8560 |  | Boiler15 | Boiler Type |  |  | 0-None 1-EMS 2-SAFe 3-SEVEN_POLE 4-SLAVE_CBC |  | int
INPUT_REGISTER | Read | 8561 |  | Boiler15 | Flow temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 8562 |  | Boiler15 | Flow temperature rate of change |  |  |  | K/min | signed int | x10
INPUT_REGISTER | Read | 8563 |  | Boiler15 | Return Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 8564 |  | Boiler15 | Current power |  |  |  | % | int
INPUT_REGISTER | Read | 8565 |  | Boiler15 | Load limit continuous |  |  |  | % | int
INPUT_REGISTER | Read | 8566 |  | Boiler15 | Operating temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 8567 |  | Boiler15 | Maximum power |  |  |  | kW | int
INPUT_REGISTER | Read | 8568 |  | Boiler15 | Minimum relative power |  |  |  | % | int
INPUT_REGISTER | Read | 8569 |  | Boiler15 | Burner type |  |  | 0-Modulating 1-One_Stage 2-Two_Stage |  | int
INPUT_REGISTER | Read | 8570 |  | Boiler15 | Fuel type |  |  | 0-Gas 1-Oil |  | int
INPUT_REGISTER | Read | 8571 |  | Boiler15 | Maximum Temp Setpoint |  |  |  | °C | int
INPUT_REGISTER | Read | 8572 |  | Boiler15 | Hmi State |  |  | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 8573 |  | Boiler15 | bitblock |  |  |  |  | int
| Read |  | 0 | Boiler15 | isControlPossible |  |  |  |  | bit
| Read |  | 1 | Boiler15 | isForcedFlow |  |  |  |  | bit
| Read |  | 2 | Boiler15 | isTakeHeat |  |  |  |  | bit
| Read |  | 3 | Boiler15 | isLoadLimitDigital |  |  |  |  | bit
| Read |  | 4 | Boiler15 | isLoadLimitFastReduction |  |  |  |  | bit
| Read |  | 5 | Boiler15 | isBurnerOn |  |  |  |  | bit
| Read |  | 6 | Boiler15 | isRequestLeading |  |  |  |  | bit
| Read |  | 7 | Boiler15 | isRequestPriority |  |  |  |  | bit
| Read |  | 8 | Boiler15 | isRequestFlowControl |  |  |  |  | bit
| Read |  | 9 | Boiler15 | isRequestPowerControl |  |  |  |  | bit
| Read |  | 10 | Boiler15 | isLocked |  |  |  |  | bit
| Read |  | 11 | Boiler15 | isBlocked |  |  |  |  | bit
| Read |  | 12 | Boiler15 | isInMaintenance |  |  |  |  | bit
INPUT_REGISTER | Read | 8574 |  | Boiler15 | Request Working Mode |  |  | 0-Off 1-Take_Heat 2-Give_Heat |  | int
INPUT_REGISTER | Read | 8575 |  | Boiler15 | Request Temperature Setpoint |  |  |  | °C | int
INPUT_REGISTER | Read | 8576 |  | Boiler15 | Request Power Setpoint |  |  |  | % | int
INPUT_REGISTER | Read | 8577 |  | Boiler15 | Current Pressure |  |  |  | bar | signed int | x10
INPUT_REGISTER | Read | 8578 |  | Boiler15 | Error Cause Code |  |  |  |  | int
INPUT_REGISTER | Read | 8579 |  | Boiler15 | Error Display Code |  |  |  |  | int
INPUT_REGISTER | Read | 8580 |  | Boiler15 | Cascade Start Index | 1 | 16 |  |  | int
INPUT_REGISTER | Read | 8581 |  | Boiler15 | Number of Starts |  |  |  |  | long
INPUT_REGISTER | Read | 8583 |  | Boiler15 | Operating Time |  |  |  | min | long
INPUT_REGISTER | Read | 8585 |  | Boiler15 | Valve Position |  |  |  | % | int
INPUT_REGISTER | Read | 8586 |  | Boiler15 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 8587 |  | Boiler15 | Stb temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 8600 |  | Boiler16 | Boiler Type |  |  | 0-None 1-EMS 2-SAFe 3-SEVEN_POLE 4-SLAVE_CBC |  | int
INPUT_REGISTER | Read | 8601 |  | Boiler16 | Flow temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 8602 |  | Boiler16 | Flow temperature rate of change |  |  |  | K/min | signed int | x10
INPUT_REGISTER | Read | 8603 |  | Boiler16 | Return Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 8604 |  | Boiler16 | Current power |  |  |  | % | int
INPUT_REGISTER | Read | 8605 |  | Boiler16 | Load limit continuous |  |  |  | % | int
INPUT_REGISTER | Read | 8606 |  | Boiler16 | Operating temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 8607 |  | Boiler16 | Maximum power |  |  |  | kW | int
INPUT_REGISTER | Read | 8608 |  | Boiler16 | Minimum relative power |  |  |  | % | int
INPUT_REGISTER | Read | 8609 |  | Boiler16 | Burner type |  |  | 0-Modulating 1-One_Stage 2-Two_Stage |  | int
INPUT_REGISTER | Read | 8610 |  | Boiler16 | Fuel type |  |  | 0-Gas 1-Oil |  | int
INPUT_REGISTER | Read | 8611 |  | Boiler16 | Maximum Temp Setpoint |  |  |  | °C | int
INPUT_REGISTER | Read | 8612 |  | Boiler16 | Hmi State |  |  | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 8613 |  | Boiler16 | bitblock |  |  |  |  | int
| Read |  | 0 | Boiler16 | isControlPossible |  |  |  |  | bit
| Read |  | 1 | Boiler16 | isForcedFlow |  |  |  |  | bit
| Read |  | 2 | Boiler16 | isTakeHeat |  |  |  |  | bit
| Read |  | 3 | Boiler16 | isLoadLimitDigital |  |  |  |  | bit
| Read |  | 4 | Boiler16 | isLoadLimitFastReduction |  |  |  |  | bit
| Read |  | 5 | Boiler16 | isBurnerOn |  |  |  |  | bit
| Read |  | 6 | Boiler16 | isRequestLeading |  |  |  |  | bit
| Read |  | 7 | Boiler16 | isRequestPriority |  |  |  |  | bit
| Read |  | 8 | Boiler16 | isRequestFlowControl |  |  |  |  | bit
| Read |  | 9 | Boiler16 | isRequestPowerControl |  |  |  |  | bit
| Read |  | 10 | Boiler16 | isLocked |  |  |  |  | bit
| Read |  | 11 | Boiler16 | isBlocked |  |  |  |  | bit
| Read |  | 12 | Boiler16 | isInMaintenance |  |  |  |  | bit
INPUT_REGISTER | Read | 8614 |  | Boiler16 | Request Working Mode |  |  | 0-Off 1-Take_Heat 2-Give_Heat |  | int
INPUT_REGISTER | Read | 8615 |  | Boiler16 | Request Temperature Setpoint |  |  |  | °C | int
INPUT_REGISTER | Read | 8616 |  | Boiler16 | Request Power Setpoint |  |  |  | % | int
INPUT_REGISTER | Read | 8617 |  | Boiler16 | Current Pressure |  |  |  | bar | signed int | x10
INPUT_REGISTER | Read | 8618 |  | Boiler16 | Error Cause Code |  |  |  |  | int
INPUT_REGISTER | Read | 8619 |  | Boiler16 | Error Display Code |  |  |  |  | int
INPUT_REGISTER | Read | 8620 |  | Boiler16 | Cascade Start Index | 1 | 16 |  |  | int
INPUT_REGISTER | Read | 8621 |  | Boiler16 | Number of Starts |  |  |  |  | long
INPUT_REGISTER | Read | 8623 |  | Boiler16 | Operating Time |  |  |  | min | long
INPUT_REGISTER | Read | 8625 |  | Boiler16 | Valve Position |  |  |  | % | int
INPUT_REGISTER | Read | 8626 |  | Boiler16 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 8627 |  | Boiler16 | Stb temperature |  |  |  | °C | signed int | x10

## Slave01
Register Type | Permissions | Address | Bitblock Bit | Component | Name | Min | Max | Range | Unit | DataType | Float to Int Factor
HOLDING_REGISTER | Write | 507 |  | DomesticHotWater Zm/Ems | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 508 |  | DomesticHotWater Zm/Ems | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 509 |  | DomesticHotWater Zm/Ems | Thermal Disinfection Setpoint | 65 | 75 |  | °C | int | x10
HOLDING_REGISTER | Write | 510 |  | DomesticHotWater Zm | Setpoint Auto Day | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 511 |  | DomesticHotWater Zm | Setpoint Auto Night | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 512 |  | DomesticHotWater Zm | Setpoint Manual Day | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 513 |  | DomesticHotWater Zm | Setpoint Manual Night | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 514 |  | DomesticHotWater Zm | Setpoint Holiday | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 515 |  | DomesticHotWater Zm/Ems | Circulation Pump Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 516 |  | DomesticHotWater Zm/Ems | Circulation Pump Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 517 |  | DomesticHotWater Zm/Ems | Disinfection Frequency | 0 | 7 | 0-Daily 1-Monday 2-Tuesday 3-Wednesday 4-Thursday 5-Friday 6-Saturday 7-Sunday |  | int
HOLDING_REGISTER | Write | 518 |  | DomesticHotWater Zm/Ems | Disinfection Start Hour | 0 | 23 |  | h | int
HOLDING_REGISTER | Write | 521 |  | DomesticHotWater Fm | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 522 |  | DomesticHotWater Fm | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 523 |  | DomesticHotWater Fm | Thermal Disinfection Setpoint | 65 | 75 |  | °C | int | x10
HOLDING_REGISTER | Write | 524 |  | DomesticHotWater Fm | Setpoint Auto Day | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 525 |  | DomesticHotWater Fm | Setpoint Auto Night | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 526 |  | DomesticHotWater Fm | Setpoint Manual Day | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 527 |  | DomesticHotWater Fm | Setpoint Manual Night | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 528 |  | DomesticHotWater Fm | Setpoint Holiday | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 529 |  | DomesticHotWater Fm | Circulation Pump Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 530 |  | DomesticHotWater Fm | Circulation Pump Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 531 |  | DomesticHotWater Fm | Disinfection Frequency | 0 | 7 | 0-Daily 1-Monday 2-Tuesday 3-Wednesday 4-Thursday 5-Friday 6-Saturday 7-Sunday |  | int
HOLDING_REGISTER | Write | 532 |  | DomesticHotWater Fm | Disinfection Start Hour | 0 | 23 |  | h | int
HOLDING_REGISTER | Read | 539 |  | Boiler | Control Type | 0 | 4 | 0-None 1-Safe 2-Ems 3-7Pole 4-Substation |  | int
HOLDING_REGISTER | Write | 543 |  | AlternativeHeatSource | Operation Mode Request Auto Day | 20 | 99 |  | °C | int
HOLDING_REGISTER | Write | 544 |  | AlternativeHeatSource | Operation Mode Request Auto Night | 20 | 99 |  | °C | int
HOLDING_REGISTER | Write | 545 |  | AlternativeHeatSource | Operation Mode Request Manual Day | 20 | 99 |  | °C | int
HOLDING_REGISTER | Write | 546 |  | AlternativeHeatSource | Operation Mode Request Manual Night | 20 | 99 |  | °C | int
HOLDING_REGISTER | Write | 547 |  | AlternativeHeatSource | Operation Mode Request Holiday | 20 | 99 |  | °C | int
HOLDING_REGISTER | Write | 548 |  | AlternativeHeatSource | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 549 |  | AlternativeHeatSource | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 550 |  | AlternativeHeatSource | Return Control Setpoint User | 10 | 70 |  | °C | int
HOLDING_REGISTER | Write | 557 |  | HydraulicCircuit Zm | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 558 |  | HydraulicCircuit Zm | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 559 |  | HydraulicCircuit Zm | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 560 |  | HydraulicCircuit Zm | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 561 |  | HydraulicCircuit Zm | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 562 |  | HydraulicCircuit Zm | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 563 |  | HydraulicCircuit Zm | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 564 |  | HydraulicCircuit Zm | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 570 |  | HydraulicCircuit 1 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 571 |  | HydraulicCircuit 1 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 572 |  | HydraulicCircuit 1 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 573 |  | HydraulicCircuit 1 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 574 |  | HydraulicCircuit 1 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 575 |  | HydraulicCircuit 1 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 576 |  | HydraulicCircuit 1 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 577 |  | HydraulicCircuit 1 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 583 |  | HydraulicCircuit 2 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 584 |  | HydraulicCircuit 2 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 585 |  | HydraulicCircuit 2 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 586 |  | HydraulicCircuit 2 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 587 |  | HydraulicCircuit 2 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 588 |  | HydraulicCircuit 2 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 589 |  | HydraulicCircuit 2 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 590 |  | HydraulicCircuit 2 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 596 |  | HydraulicCircuit 3 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 597 |  | HydraulicCircuit 3 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 598 |  | HydraulicCircuit 3 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 599 |  | HydraulicCircuit 3 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 600 |  | HydraulicCircuit 3 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 601 |  | HydraulicCircuit 3 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 602 |  | HydraulicCircuit 3 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 603 |  | HydraulicCircuit 3 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 609 |  | HydraulicCircuit 4 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 610 |  | HydraulicCircuit 4 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 611 |  | HydraulicCircuit 4 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 612 |  | HydraulicCircuit 4 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 613 |  | HydraulicCircuit 4 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 614 |  | HydraulicCircuit 4 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 615 |  | HydraulicCircuit 4 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 616 |  | HydraulicCircuit 4 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 622 |  | HydraulicCircuit 5 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 623 |  | HydraulicCircuit 5 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 624 |  | HydraulicCircuit 5 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 625 |  | HydraulicCircuit 5 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 626 |  | HydraulicCircuit 5 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 627 |  | HydraulicCircuit 5 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 628 |  | HydraulicCircuit 5 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 629 |  | HydraulicCircuit 5 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 635 |  | HydraulicCircuit 6 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 636 |  | HydraulicCircuit 6 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 637 |  | HydraulicCircuit 6 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 638 |  | HydraulicCircuit 6 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 639 |  | HydraulicCircuit 6 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 640 |  | HydraulicCircuit 6 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 641 |  | HydraulicCircuit 6 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 642 |  | HydraulicCircuit 6 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 648 |  | HydraulicCircuit 7 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 649 |  | HydraulicCircuit 7 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 650 |  | HydraulicCircuit 7 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 651 |  | HydraulicCircuit 7 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 652 |  | HydraulicCircuit 7 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 653 |  | HydraulicCircuit 7 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 654 |  | HydraulicCircuit 7 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 655 |  | HydraulicCircuit 7 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 661 |  | HydraulicCircuit 8 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 662 |  | HydraulicCircuit 8 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 663 |  | HydraulicCircuit 8 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 664 |  | HydraulicCircuit 8 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 665 |  | HydraulicCircuit 8 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 666 |  | HydraulicCircuit 8 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 667 |  | HydraulicCircuit 8 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 668 |  | HydraulicCircuit 8 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 701 |  | Heat Pump | Heat demand source | 0 | 2 | 0-Scheduler 1-System 2-Max_system_scheduler |  | int
HOLDING_REGISTER | Read | 921 |  | Fresh Water Characteristics 3 | DHU Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 922 |  | Fresh Water Characteristics 3 | Extra Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 923 |  | Fresh Water Characteristics 3 | Maximum DHW Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 924 |  | Fresh Water Characteristics 3 | On High Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 925 |  | Fresh Water Characteristics 3 | On Low Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 926 |  | Fresh Water Characteristics 3 | Fresh Water Type | 0 | 3 | 0-15/20l/min 1-27l/min 2-40l/min 3-60l/min |  | int
HOLDING_REGISTER | Read | 927 |  | Fresh Water Characteristics 3 | Enable Alarm Output | 0 | 2 | 0-No 1-Yes 2-Inverted |  | int
HOLDING_REGISTER | Read | 928 |  | Fresh Water Characteristics 3 | Buffer Cylinder Temperature Offset |  |  |  | K | int
HOLDING_REGISTER | Read | 929 |  | Fresh Water Characteristics 3 | hrBitblock |  |  |  |  | int
| Read |  | 0 | Fresh Water | Buffer Cylinder Temperature Optimization Enabled |  |  |  |  | bit
| Read |  | 1 | Fresh Water | Impulse Enabled |  |  |  |  | bit
| Read |  | 2 | Fresh Water | Time Program Enabled |  |  |  |  | bit
HOLDING_REGISTER | Read | 930 |  | Fresh Water Characteristics 3 | Minimum Buffer Cylinder Temperature Offset |  |  |  | K | int
HOLDING_REGISTER | Read | 931 |  | Fresh Water Characteristics 2 | Circulation Pump Runs per Hour | 0 | 7 | 0-Undefined 1-1x3_minutes/h 2-2x3_minutes/h 3-3x3_minutes/h 4-4x3_minutes/h 5-5x3_minutes/h 6-6x3_minutes/h 7-Permanent |  | int
HOLDING_REGISTER | Read | 932 |  | Fresh Water Characteristics 2 | Swich Hysteresis |  |  |  | K | int
HOLDING_REGISTER | Read | 933 |  | Fresh Water Characteristics 2 | Thermal Disinfection Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 934 |  | Fresh Water Characteristics 2 | Pre Heat Maximum Temperature |  |  |  | °C | int
INPUT_REGISTER | Read | 500 |  | System | Own Outdoor temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 501 |  | System | Damped Own outdoor temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 504 |  | System | Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 508 |  | System | Active Functions 1 |  |  |  |  | int
INPUT_REGISTER | Read | 509 |  | System | Active Functions 2 |  |  |  |  | int
INPUT_REGISTER | Read | 515 |  | DomesticHotWater Zm | Charge Pump Running | 0 | 4 | 0-Stopping 1-Starting 2-Running 3-Off 4-Error |  | int
INPUT_REGISTER | Read | 516 |  | DomesticHotWater Zm | Circulation Pump Running | 0 | 4 | 0-Stopping 1-Starting 2-Running 3-Off 4-Error |  | int
INPUT_REGISTER | Read | 517 |  | DomesticHotWater Zm | Hydraulic State | 0 | 7 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Cold_load 6-Post_purge 7-Condense_protection |  | int
INPUT_REGISTER | Read | 518 |  | DomesticHotWater Zm/Ems | Thermal Disinfection Status | 0 | 3 | 0-Off 1-On 2-Success 3-Error |  | int
INPUT_REGISTER | Read | 519 |  | DomesticHotWater Zm/Ems | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 520 |  | DomesticHotWater Zm/Ems | Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 521 |  | DomesticHotWater Zm/Ems | Current Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 531 |  | DomesticHotWater Fm | Charge Pump Running | 0 | 4 | 0-Stopping 1-Starting 2-Running 3-Off 4-Error |  | int
INPUT_REGISTER | Read | 532 |  | DomesticHotWater Fm | Circulation Pump Running | 0 | 4 | 0-Stopping 1-Starting 2-Running 3-Off 4-Error |  | int
INPUT_REGISTER | Read | 533 |  | DomesticHotWater Fm | Hydraulic State | 0 | 7 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Cold_load 6-Post_purge 7-Condense_protection |  | int
INPUT_REGISTER | Read | 534 |  | DomesticHotWater Fm | Thermal Disinfection Status | 0 | 3 | 0-Off 1-On 2-Success 3-Error |  | int
INPUT_REGISTER | Read | 535 |  | DomesticHotWater Fm | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 536 |  | DomesticHotWater Fm | Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 537 |  | DomesticHotWater Fm | Current Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER |  | 547 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 548 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 550 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 552 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 553 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 554 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 555 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 556 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 559 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 560 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER | Read | 563 |  | AlternativeHeatSource | Operating hours |  |  |  | h | long
INPUT_REGISTER | Read | 565 |  | AlternativeHeatSource | Heat Source Starts |  |  |  |  | long
INPUT_REGISTER | Read | 567 |  | AlternativeHeatSource | Heat Source Hours to Maintenance |  |  |  | h | int
INPUT_REGISTER | Read | 569 |  | AlternativeHeatSource | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
| Read |  | 0 | AlternativeHeatSource | Is Heat Source On |  |  |  |  | bit
| Read |  | 1 | AlternativeHeatSource | Is Heat Source On Request |  |  |  |  | bit
INPUT_REGISTER | Read | 587 |  | HydraulicCircuit Zm | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 588 |  | HydraulicCircuit Zm | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 589 |  | HydraulicCircuit Zm | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 590 |  | HydraulicCircuit Zm | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 591 |  | HydraulicCircuit Zm | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 592 |  | HydraulicCircuit Zm | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 593 |  | HydraulicCircuit Zm | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 594 |  | HydraulicCircuit Zm | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 595 |  | HydraulicCircuit Zm | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 599 |  | HydraulicCircuit 1 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 600 |  | HydraulicCircuit 1 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 601 |  | HydraulicCircuit 1 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 602 |  | HydraulicCircuit 1 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 603 |  | HydraulicCircuit 1 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 604 |  | HydraulicCircuit 1 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 605 |  | HydraulicCircuit 1 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 606 |  | HydraulicCircuit 1 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 607 |  | HydraulicCircuit 1 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 612 |  | HydraulicCircuit 2 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 613 |  | HydraulicCircuit 2 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 614 |  | HydraulicCircuit 2 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 615 |  | HydraulicCircuit 2 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 616 |  | HydraulicCircuit 2 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 617 |  | HydraulicCircuit 2 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 618 |  | HydraulicCircuit 2 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 619 |  | HydraulicCircuit 2 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 620 |  | HydraulicCircuit 2 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 625 |  | HydraulicCircuit 3 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 626 |  | HydraulicCircuit 3 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 627 |  | HydraulicCircuit 3 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 628 |  | HydraulicCircuit 3 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 629 |  | HydraulicCircuit 3 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 630 |  | HydraulicCircuit 3 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 631 |  | HydraulicCircuit 3 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 632 |  | HydraulicCircuit 3 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 633 |  | HydraulicCircuit 3 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 638 |  | HydraulicCircuit 4 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 639 |  | HydraulicCircuit 4 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 640 |  | HydraulicCircuit 4 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 641 |  | HydraulicCircuit 4 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 642 |  | HydraulicCircuit 4 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 643 |  | HydraulicCircuit 4 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 644 |  | HydraulicCircuit 4 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 645 |  | HydraulicCircuit 4 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 646 |  | HydraulicCircuit 4 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 651 |  | HydraulicCircuit 5 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 652 |  | HydraulicCircuit 5 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 653 |  | HydraulicCircuit 5 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 654 |  | HydraulicCircuit 5 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 655 |  | HydraulicCircuit 5 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 656 |  | HydraulicCircuit 5 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 657 |  | HydraulicCircuit 5 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 658 |  | HydraulicCircuit 5 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 659 |  | HydraulicCircuit 5 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 664 |  | HydraulicCircuit 6 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 665 |  | HydraulicCircuit 6 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 666 |  | HydraulicCircuit 6 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 667 |  | HydraulicCircuit 6 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 668 |  | HydraulicCircuit 6 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 669 |  | HydraulicCircuit 6 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 670 |  | HydraulicCircuit 6 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 671 |  | HydraulicCircuit 6 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 672 |  | HydraulicCircuit 6 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 677 |  | HydraulicCircuit 7 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 678 |  | HydraulicCircuit 7 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 679 |  | HydraulicCircuit 7 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 680 |  | HydraulicCircuit 7 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 681 |  | HydraulicCircuit 7 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 682 |  | HydraulicCircuit 7 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 683 |  | HydraulicCircuit 7 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 684 |  | HydraulicCircuit 7 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 685 |  | HydraulicCircuit 7 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 690 |  | HydraulicCircuit 8 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 691 |  | HydraulicCircuit 8 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 692 |  | HydraulicCircuit 8 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 693 |  | HydraulicCircuit 8 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 694 |  | HydraulicCircuit 8 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 695 |  | HydraulicCircuit 8 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 696 |  | HydraulicCircuit 8 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 697 |  | HydraulicCircuit 8 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 698 |  | HydraulicCircuit 8 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 703 |  | i2c | Global Error State | 0 | 4 | 0-No_Error 1-i2c_driver_error 2-Wrong_Cycle_Time 3-Missing_Module_Slot 4-Module_Slot_Error |  | int
INPUT_REGISTER | Read | 704 |  | i2c | Slot1 Module Detected |  |  | 0-Unknown 1-None 22-FM_CM 25-FM_SI 28-FM_MM 29-FM_MW 30-FM_AM 31-FM_CM2 |  | int
INPUT_REGISTER | Read | 705 |  | i2c | Slot1 Error State |  |  | 0-No_Error 1-No_Response 2-Wrong_Module 3-Unsupported_Module 4-Internal_Sw_Error 5-Communication_Failed 6-Internal_Module_Error 7-Module_Not_Supported_Current_Variant 8-Module_Not_Suppported_In_Slot 9-Module_Count_Too_High 10-Module_Not_Supported_With_Connected_Boiler_Type |  | int
INPUT_REGISTER | Read | 706 |  | i2c | Slot2 Module Detected |  |  | 0-Unknown 1-None 22-FM_CM 25-FM_SI 28-FM_MM 29-FM_MW 30-FM_AM 31-FM_CM2 |  | int
INPUT_REGISTER | Read | 707 |  | i2c | Slot2 Error State |  |  | 0-No_Error 1-No_Response 2-Wrong_Module 3-Unsupported_Module 4-Internal_Sw_Error 5-Communication_Failed 6-Internal_Module_Error 7-Module_Not_Supported_Current_Variant 8-Module_Not_Suppported_In_Slot 9-Module_Count_Too_High 10-Module_Not_Supported_With_Connected_Boiler_Type |  | int
INPUT_REGISTER | Read | 708 |  | i2c | Slot3 Module Detected |  |  | 0-Unknown 1-None 22-FM_CM 25-FM_SI 28-FM_MM 29-FM_MW 30-FM_AM 31-FM_CM2 |  | int
INPUT_REGISTER | Read | 709 |  | i2c | Slot3 Error State |  |  | 0-No_Error 1-No_Response 2-Wrong_Module 3-Unsupported_Module 4-Internal_Sw_Error 5-Communication_Failed 6-Internal_Module_Error 7-Module_Not_Supported_Current_Variant 8-Module_Not_Suppported_In_Slot 9-Module_Count_Too_High 10-Module_Not_Supported_With_Connected_Boiler_Type |  | int
INPUT_REGISTER | Read | 710 |  | i2c | Slot4 Module Detected |  |  | 0-Unknown 1-None 22-FM_CM 25-FM_SI 28-FM_MM 29-FM_MW 30-FM_AM 31-FM_CM2 |  | int
INPUT_REGISTER | Read | 711 |  | i2c | Slot4 Error State |  |  | 0-No_Error 1-No_Response 2-Wrong_Module 3-Unsupported_Module 4-Internal_Sw_Error 5-Communication_Failed 6-Internal_Module_Error 7-Module_Not_Supported_Current_Variant 8-Module_Not_Suppported_In_Slot 9-Module_Count_Too_High 10-Module_Not_Supported_With_Connected_Boiler_Type |  | int
INPUT_REGISTER | Read | 712 |  | i2c | Slot A Module Detected |  |  | 0-Unknown 1-None 26-ZM5313 27-ZM5311 |  | int
INPUT_REGISTER | Read | 713 |  | i2c | Slot A Error State |  |  | 0-No_Error 1-No_Response 2-Wrong_Module 3-Unsupported_Module 4-Internal_Sw_Error 5-Communication_Failed 6-Internal_Module_Error 7-Module_Not_Supported_Current_Variant 8-Module_Not_Suppported_In_Slot 9-Module_Count_Too_High 10-Module_Not_Supported_With_Connected_Boiler_Type |  | int
INPUT_REGISTER | Read | 714 |  | i2c | irBitblock |  |  |  |  | int
| Read |  | 0 | i2c | Component Error |  |  |  |  | bit
INPUT_REGISTER | Read | 725 |  | fm-si | irBitblock |  |  |  |  | int
| Read |  | 0 | fm-si | Input 1 Error |  |  |  |  | bit
| Read |  | 1 | fm-si | Input 2 Error |  |  |  |  | bit
| Read |  | 2 | fm-si | Input 3 Error |  |  |  |  | bit
| Read |  | 3 | fm-si | Input 4 Error |  |  |  |  | bit
| Read |  | 4 | fm-si | Input 5 Error |  |  |  |  | bit
INPUT_REGISTER | Read | 732 |  | Sdc | Demand Mode (Low Priority) | 0 | 2 | 0-Off 1-Take_Heat 2-Give_Heat |  | int
INPUT_REGISTER | Read | 733 |  | Sdc | Demand Flow Temp (Low Priority) |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 734 |  | Sdc | Demand Mode (High Priority) | 0 | 2 | 0-Off 1-Take_Heat 2-Give_Heat |  | int
INPUT_REGISTER | Read | 735 |  | Sdc | Demand Flow Temp (High Priority) |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 739 |  | Heat Pump | System return temperature for HP heating buffer |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 740 |  | Heat Pump | Buffer mid temperature for HP heating buffer |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 741 |  | Heat Pump | Buffer top temperature for HP heating buffer |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 742 |  | Heat Pump | Buffer bottom temperature for HP heating buffer |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 743 |  | Heat Pump | Return temperature FWR |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 744 |  | Heat Pump | Flow temperature FWV |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 745 |  | Heat Pump | Flow temperature HP |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 746 |  | Heat Pump | Return temperature HP |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 747 |  | Heat Pump | HMI State of HP Component | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 748 |  | Heat Pump | HP current heat output |  |  |  | kW | signed int | x10
INPUT_REGISTER | Read | 749 |  | Heat Pump | HP current electrical power consumption | 0 | 10000 |  | kW | int | x10
INPUT_REGISTER | Read | 750 |  | Heat Pump | HP Smart grid mode | 0 | 3 | 0-normal_charging_grid 1-low_charging_grid 2-high_charging_grid 3-free_charging_grid |  | int
INPUT_REGISTER | Read | 751 |  | Heat Pump | Heat demand temperature set point |  |  |  | °C | int
INPUT_REGISTER | Read | 752 |  | Heat Pump | heatPumpStatusIrBitblock | 0 |  |  |  | int
INPUT_REGISTER | Read | 753 |  | Heat Pump | Ambient Temperature HP |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 754 |  | Heat Pump | HP silent mode | 0 | 3 | 0-standard_mode 1-silent_mode 2-super_silent_mode 3-night_mode |  | int
INPUT_REGISTER | Read | 755 |  | Heat Pump | Heat Pump Heat Request Temperature |  |  |  | °C | int
INPUT_REGISTER | Read | 756 |  | Heat Pump | heatPumpIrBitblock |  |  |  |  | int
INPUT_REGISTER | Read | 765 |  | System | Open Notifications Count |  |  |  |  | int
INPUT_REGISTER | Read | 766 |  | System | Error Key 5 |  |  |  |  | long
INPUT_REGISTER | Read | 768 |  | System | Error Key 6 |  |  |  |  | long
INPUT_REGISTER | Read | 770 |  | System | Error Key 7 |  |  |  |  | long
INPUT_REGISTER | Read | 772 |  | System | Error Key 8 |  |  |  |  | long
INPUT_REGISTER | Read | 774 |  | System | Error Key 9 |  |  |  |  | long
INPUT_REGISTER | Read | 776 |  | System | Error Key 10 |  |  |  |  | long
INPUT_REGISTER | Read | 778 |  | Chp / EC Power | Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 779 |  | Chp / EC Power | Return Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 780 |  | Chp | Flue Gas Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 781 |  | Chp | Motor Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 782 |  | Chp / EC Power | Current Generator Power |  |  |  | kW | int
INPUT_REGISTER | Read | 783 |  | Chp | Current Power Setpoint |  |  |  | kW | int
INPUT_REGISTER | Read | 784 |  | Chp / EC Power | Operation Hours |  |  |  | h | long
INPUT_REGISTER | Read | 786 |  | Chp / EC Power | Number of starts |  |  |  |  | long
INPUT_REGISTER | Read | 788 |  | Chp / EC Power | Hours to Maintenance |  |  |  | h | int
INPUT_REGISTER | Read | 790 |  | Chp | Output Power Setpoint |  |  |  | kW | int
INPUT_REGISTER | Read | 791 |  | Chp | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 796 |  | Chp | irBitblock |  |  |  |  | int
| Read |  | 0 | Chp | Warning |  |  |  |  | bit
| Read |  | 1 | Chp / EC Power | Malfunction |  |  |  |  | bit
| Read |  | 2 | Chp / EC Power | Controlled Shutdown |  |  |  |  | bit
| Read |  | 3 | Chp / EC Power | Generator On |  |  |  |  | bit
| Read |  | 4 | Chp | Automatic On |  |  |  |  | bit
| Read |  | 5 | Chp / EC Power | Automatic Ready |  |  |  |  | bit
| Read |  | 11 | Chp / EC Power | Output On Request |  |  |  |  | bit
INPUT_REGISTER | Read | 804 |  | Water Treatment Module | Program Step |  |  | 20-140: Desalination not active 10000-10810: One time desalination 20000-20810: Automatic desalination 30000-30260: Stationary operation |  | int
INPUT_REGISTER | Read | 805 |  | Water Treatment Module | Temperature Desalinization |  |  |  | °C | int | x10
INPUT_REGISTER | Read | 806 |  | Water Treatment Module | Volume Flow |  |  |  | L/min | int | x10
INPUT_REGISTER | Read | 807 |  | Water Treatment Module | Conductivity system |  |  |  | uS/cm | int | x10
INPUT_REGISTER | Read | 808 |  | Water Treatment Module | Conductivity cartridge |  |  |  | uS/cm | int | x10
INPUT_REGISTER | Read | 809 |  | Water Treatment Module | Cartridge Capacity |  |  |  | % | int
INPUT_REGISTER | Read | 813 |  | Solar Data | Collector temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 814 |  | Solar Data | Temperature cylinder bottom |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 815 |  | Solar Data | Solar pump modulation setpoint |  |  |  | % | int
INPUT_REGISTER | Read | 816 |  | Solar | Solar pump status | 0 | 19 | 1-TestMod 2-BlckProt 3-No heat 4-Ht avail 5-SolOff 6-MaxCyl 7-MaxColl 8-MinColl 9-FrostP 10-VacFct 11-SwChck 12-MixPrio 13-Switch 14-Priority 15-ThermD 16-MixCal 17-MixOpn 18-MixCl 19-MixOff |  | int
INPUT_REGISTER | Read | 817 |  | Solar Data | Heat exchanger temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 818 |  | Solar Data | Heat exchanger pump modulation setpoint |  |  |  | % | int
INPUT_REGISTER | Read | 819 |  | Solar | Heat exchanger pump status | 0 | 19 | 1-TestMod 2-BlckProt 3-No heat 4-Ht avail 5-SolOff 6-MaxCyl 7-MaxColl 8-MinColl 9-FrostP 10-VacFct 11-SwChck 12-MixPrio 13-Switch 14-Priority 15-ThermD 16-MixCal 17-MixOpn 18-MixCl 19-MixOff |  | int
INPUT_REGISTER | Read | 820 |  | Solar Data | Temperature cylinder 3 top |  |  |  | °C | int | x10
INPUT_REGISTER | Read | 821 |  | Solar Data | Reload pump modulation setpoint |  |  |  | % | int
INPUT_REGISTER | Read | 822 |  | Solar | Reload pump status | 0 | 19 | 1-TestMod 2-BlckProt 3-No heat 4-Ht avail 5-SolOff 6-MaxCyl 7-MaxColl 8-MinColl 9-FrostP 10-VacFct 11-SwChck 12-MixPrio 13-Switch 14-Priority 15-ThermD 16-MixCal 17-MixOpn 18-MixCl 19-MixOff |  | int
INPUT_REGISTER | Read | 823 |  | Solar | Pump therm. disinfect. status | 0 | 19 | 1-TestMod 2-BlckProt 3-No heat 4-Ht avail 5-SolOff 6-MaxCyl 7-MaxColl 8-MinColl 9-FrostP 10-VacFct 11-SwChck 12-MixPrio 13-Switch 14-Priority 15-ThermD 16-MixCal 17-MixOpn 18-MixCl 19-MixOff |  | int
INPUT_REGISTER | Read | 824 |  | Solar Yield | Flow temperature heat meter |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 825 |  | Solar Yield | Return temperature heat meter |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 826 |  | Solar Yield | Heat count pulse counter | 0 | 15 |  |  | int
INPUT_REGISTER | Read | 827 |  | Solar Yield | Solar yield per month |  |  |  | kWh | long | x10
INPUT_REGISTER | Read | 829 |  | Solar Yield | Solar yield per year |  |  |  | kWh | long | x10
INPUT_REGISTER | Read | 831 |  | Solar Yield | Last hour solar yield |  |  |  | kWh | long | x10
INPUT_REGISTER | Read | 833 |  | Solar Yield | Solar yield per day |  |  |  | kWh | long | x10
INPUT_REGISTER | Read | 835 |  | Solar Yield | Solar yield since installation |  |  |  | kWh | long | x10
INPUT_REGISTER | Read | 837 |  | Solar | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 838 |  | Solar Data | Hydraulic configuration |  |  |  |  | int
| Read |  | 0 | Solar | Option 1 active |  |  |  |  | bit
| Read |  | 1 | Solar | Option A active |  |  |  |  | bit
| Read |  | 2 | Solar | Option B active |  |  |  |  | bit
| Read |  | 3 | Solar | Option C active |  |  |  |  | bit
| Read |  | 4 | Solar | Option D active |  |  |  |  | bit
| Read |  | 5 | Solar | Option E active |  |  |  |  | bit
| Read |  | 6 | Solar | Option F active |  |  |  |  | bit
| Read |  | 7 | Solar | Option G active |  |  |  |  | bit
| Read |  | 8 | Solar | Option H active |  |  |  |  | bit
| Read |  | 9 | Solar | Option I active |  |  |  |  | bit
| Read |  | 10 | Solar | Option J active |  |  |  |  | bit
| Read |  | 11 | Solar | Option K active |  |  |  |  | bit
| Read |  | 12 | Solar | Option L active |  |  |  |  | bit
| Read |  | 13 | Solar | Option M active |  |  |  |  | bit
| Read |  | 14 | Solar | Option N active |  |  |  |  | bit
| Read |  | 15 | Solar | Option P active |  |  |  |  | bit
INPUT_REGISTER | Read | 839 |  | Solar Data | irBitblock |  |  |  |  | int
| Read |  | 0 | Solar | Is Active |  |  |  |  | bit
INPUT_REGISTER |  | 900 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 901 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 902 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 903 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 904 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 905 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 906 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 907 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 908 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 909 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 910 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 911 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 912 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 913 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER | Read | 922 |  | Energy Monitoring | Heat Output |  |  |  | kW | signed int | x10
INPUT_REGISTER | Read | 923 |  | Energy Monitoring | Gas Consumption (LCV) |  |  |  | kW | signed int | x10
INPUT_REGISTER | Read | 925 |  | Energy Monitoring | Electrical Power |  |  |  | W | int
INPUT_REGISTER | Read | 930 |  | Fresh Water Characteristics 1 | DHW Out Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 931 |  | Fresh Water Characteristics 1 | DHW Volume Flow |  |  |  | L/min | signed int | x10
INPUT_REGISTER | Read | 932 |  | Fresh Water Characteristics 1 | Prim In Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 933 |  | Fresh Water Characteristics 1 | DHW In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 934 |  | Fresh Water Characteristics 1 | Primary Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 935 |  | Fresh Water Characteristics 1 | Request DHW Out Temperature |  |  |  | °C | int
INPUT_REGISTER | Read | 936 |  | Fresh Water Characteristics 1 | Status Request DHW Out Temperature | 0 | 9 | 0-Off 1-DHWRed 2-DHW 3-Sol_red 4-Once_on 5-Therm_d 6-DlyHtUp 7-Preheat_start 8-Preheat_normal 9-No_eq |  | int
INPUT_REGISTER | Read | 937 |  | Fresh Water Characteristics 2 | Circulation Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 938 |  | Fresh Water Characteristics 2 | Status Circulation Pump | 0 | 8 | 0-Undefined 1-Test 2-BlckProt 3-No_req 4-AutoOff 5-AutoOn 6-Therm_d 7-Sys_Off 8-DlyHtUp |  | int
INPUT_REGISTER | Read | 939 |  | Fresh Water Characteristics 2 | Return Valve Modulation Request |  |  |  | % | int
INPUT_REGISTER | Read | 940 |  | Fresh Water Characteristics 2 | Valve State | 0 | 5 | 0-Undefined 1-TestMod 2-BlckProt 3-Mix_cl 4-Mix_opn 5-Sys_Off |  | int
INPUT_REGISTER | Read | 941 |  | Fresh Water Characteristics 2 | Return Valve Buffer Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 942 |  | Fresh Water Characteristics 2 | Disinfection Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 943 |  | Fresh Water Characteristics 2 | Pump State | 0 | 5 | 0-Undefined 1-TestMod 2-BlckPro 3-No_eq 4-Ht_req 5-Sys_Off |  | int
INPUT_REGISTER | Read | 944 |  | Fresh Water Characteristics 1 | DHW Valve Power |  |  |  | % | int
INPUT_REGISTER | Read | 945 |  | Fresh Water Characteristics 2 | Total Flow |  |  |  | L/min | int | x10
INPUT_REGISTER | Read | 946 |  | Fresh Water 2 | Module 2 DHW Out Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 947 |  | Fresh Water 2 | Module 2 DHW Volume Flow |  |  |  | L/min | signed int | x10
INPUT_REGISTER | Read | 948 |  | Fresh Water 2 | Module 2 Prim In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 949 |  | Fresh Water 2 | Module 2 DHW In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 950 |  | Fresh Water 2 | Module 2 DHW Valve Power |  |  |  | % | int
INPUT_REGISTER | Read | 951 |  | Fresh Water 2 | Module 2 Prim Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 952 |  | Fresh Water 2 | Module 2 Status Prim Pump |  |  |  |  | int
INPUT_REGISTER | Read | 953 |  | Fresh Water 3 | Module 3 DHW Out Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 954 |  | Fresh Water 3 | Module 3 DHW Volume Flow |  |  |  | L/min | signed int | x10
INPUT_REGISTER | Read | 955 |  | Fresh Water 3 | Module 3 Prim In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 956 |  | Fresh Water 3 | Module 3 DHW In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 957 |  | Fresh Water 3 | Module 3 DHW Valve Power |  |  |  | % | int
INPUT_REGISTER | Read | 958 |  | Fresh Water 3 | Module 3 Prim Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 959 |  | Fresh Water 3 | Module 3 Status Prim Pump |  |  |  |  | int
INPUT_REGISTER | Read | 960 |  | Fresh Water 4 | Module 4 DHW Out Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 961 |  | Fresh Water 4 | Module 4 DHW Volume Flow |  |  |  | L/min | signed int | x10
INPUT_REGISTER | Read | 962 |  | Fresh Water 4 | Module 4 Prim In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 963 |  | Fresh Water 4 | Module 4 DHW In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 964 |  | Fresh Water 4 | Module 4 DHW ValvePower |  |  |  | % | int
INPUT_REGISTER | Read | 965 |  | Fresh Water 4 | Module 4 Prim Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 966 |  | Fresh Water 4 | Module 4 Status Primary Pump |  |  |  |  | int
INPUT_REGISTER | Read | 967 |  | Fresh Water | Fresh Water Hmi State |  |  |  |  | int
INPUT_REGISTER | Read | 968 |  | Fresh Water Characteristics 3 | Fresh Water Configurations |  |  |  |  | int
| Read |  | 0 | Fresh Water | Option 2 active |  |  |  |  | bit
| Read |  | 1 | Fresh Water | Option A active |  |  |  |  | bit
| Read |  | 2 | Fresh Water | Option B active |  |  |  |  | bit
| Read |  | 3 | Fresh Water | Option C active |  |  |  |  | bit
| Read |  | 4 | Fresh Water | Option D active |  |  |  |  | bit
| Read |  | 5 | Fresh Water | Option E active |  |  |  |  | bit
| Read |  | 6 | Fresh Water | Option E active cascade module 2 active |  |  |  |  | bit
| Read |  | 7 | Fresh Water | Option E active cascade module 3 active |  |  |  |  | bit
| Read |  | 8 | Fresh Water | Option E active cascade module 4 active |  |  |  |  | bit
| Read |  | 9 | Fresh Water | Is Active |  |  |  |  | bit
INPUT_REGISTER | Read | 976 |  | System | Error Key 1 |  |  |  |  | long
INPUT_REGISTER | Read | 978 |  | System | Error Key 2 |  |  |  |  | long
INPUT_REGISTER | Read | 980 |  | System | Error Key 3 |  |  |  |  | long
INPUT_REGISTER | Read | 982 |  | System | Error Key 4 |  |  |  |  | long
INPUT_REGISTER | Read | 984 |  | System | Error 1 Extra Info (MSB) |  |  |  |  | long
INPUT_REGISTER | Read | 986 |  | System | Error 1 Extra Info (LSB) |  |  |  |  | long
INPUT_REGISTER | Read | 988 |  | System | Error 2 Extra Info (MSB) |  |  |  |  | long
INPUT_REGISTER | Read | 990 |  | System | Error 2 Extra Info (LSB) |  |  |  |  | long
INPUT_REGISTER | Read | 992 |  | System | Error 3 Extra Info (MSB) |  |  |  |  | long
INPUT_REGISTER | Read | 994 |  | System | Error 3 Extra Info (LSB) |  |  |  |  | long
INPUT_REGISTER | Read | 996 |  | System | Error 4 Extra Info (MSB) |  |  |  |  | long
INPUT_REGISTER | Read | 998 |  | System | Error 4 Extra Info (LSB) |  |  |  |  | long

## Slave02
Register Type | Permissions | Address | Bitblock Bit | Component | Name | Min | Max | Range | Unit | DataType | Float to Int Factor
HOLDING_REGISTER | Write | 1007 |  | DomesticHotWater Zm/Ems | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 1008 |  | DomesticHotWater Zm/Ems | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 1009 |  | DomesticHotWater Zm/Ems | Thermal Disinfection Setpoint | 65 | 75 |  | °C | int | x10
HOLDING_REGISTER | Write | 1010 |  | DomesticHotWater Zm | Setpoint Auto Day | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 1011 |  | DomesticHotWater Zm | Setpoint Auto Night | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 1012 |  | DomesticHotWater Zm | Setpoint Manual Day | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 1013 |  | DomesticHotWater Zm | Setpoint Manual Night | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 1014 |  | DomesticHotWater Zm | Setpoint Holiday | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 1015 |  | DomesticHotWater Zm/Ems | Circulation Pump Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 1016 |  | DomesticHotWater Zm/Ems | Circulation Pump Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 1017 |  | DomesticHotWater Zm/Ems | Disinfection Frequency | 0 | 7 | 0-Daily 1-Monday 2-Tuesday 3-Wednesday 4-Thursday 5-Friday 6-Saturday 7-Sunday |  | int
HOLDING_REGISTER | Write | 1018 |  | DomesticHotWater Zm/Ems | Disinfection Start Hour | 0 | 23 |  | h | int
HOLDING_REGISTER | Write | 1021 |  | DomesticHotWater Fm | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 1022 |  | DomesticHotWater Fm | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 1023 |  | DomesticHotWater Fm | Thermal Disinfection Setpoint | 65 | 75 |  | °C | int | x10
HOLDING_REGISTER | Write | 1024 |  | DomesticHotWater Fm | Setpoint Auto Day | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 1025 |  | DomesticHotWater Fm | Setpoint Auto Night | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 1026 |  | DomesticHotWater Fm | Setpoint Manual Day | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 1027 |  | DomesticHotWater Fm | Setpoint Manual Night | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 1028 |  | DomesticHotWater Fm | Setpoint Holiday | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 1029 |  | DomesticHotWater Fm | Circulation Pump Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 1030 |  | DomesticHotWater Fm | Circulation Pump Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 1031 |  | DomesticHotWater Fm | Disinfection Frequency | 0 | 7 | 0-Daily 1-Monday 2-Tuesday 3-Wednesday 4-Thursday 5-Friday 6-Saturday 7-Sunday |  | int
HOLDING_REGISTER | Write | 1032 |  | DomesticHotWater Fm | Disinfection Start Hour | 0 | 23 |  | h | int
HOLDING_REGISTER | Read | 1039 |  | Boiler | Control Type | 0 | 4 | 0-None 1-Safe 2-Ems 3-7Pole 4-Substation |  | int
HOLDING_REGISTER | Write | 1043 |  | AlternativeHeatSource | Operation Mode Request Auto Day | 20 | 99 |  | °C | int
HOLDING_REGISTER | Write | 1044 |  | AlternativeHeatSource | Operation Mode Request Auto Night | 20 | 99 |  | °C | int
HOLDING_REGISTER | Write | 1045 |  | AlternativeHeatSource | Operation Mode Request Manual Day | 20 | 99 |  | °C | int
HOLDING_REGISTER | Write | 1046 |  | AlternativeHeatSource | Operation Mode Request Manual Night | 20 | 99 |  | °C | int
HOLDING_REGISTER | Write | 1047 |  | AlternativeHeatSource | Operation Mode Request Holiday | 20 | 99 |  | °C | int
HOLDING_REGISTER | Write | 1048 |  | AlternativeHeatSource | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 1049 |  | AlternativeHeatSource | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 1050 |  | AlternativeHeatSource | Return Control Setpoint User | 10 | 70 |  | °C | int
HOLDING_REGISTER | Write | 1057 |  | HydraulicCircuit Zm | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 1058 |  | HydraulicCircuit Zm | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 1059 |  | HydraulicCircuit Zm | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1060 |  | HydraulicCircuit Zm | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1061 |  | HydraulicCircuit Zm | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1062 |  | HydraulicCircuit Zm | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1063 |  | HydraulicCircuit Zm | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1064 |  | HydraulicCircuit Zm | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 1070 |  | HydraulicCircuit 1 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 1071 |  | HydraulicCircuit 1 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 1072 |  | HydraulicCircuit 1 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1073 |  | HydraulicCircuit 1 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1074 |  | HydraulicCircuit 1 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1075 |  | HydraulicCircuit 1 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1076 |  | HydraulicCircuit 1 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1077 |  | HydraulicCircuit 1 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 1083 |  | HydraulicCircuit 2 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 1084 |  | HydraulicCircuit 2 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 1085 |  | HydraulicCircuit 2 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1086 |  | HydraulicCircuit 2 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1087 |  | HydraulicCircuit 2 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1088 |  | HydraulicCircuit 2 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1089 |  | HydraulicCircuit 2 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1090 |  | HydraulicCircuit 2 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 1096 |  | HydraulicCircuit 3 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 1097 |  | HydraulicCircuit 3 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 1098 |  | HydraulicCircuit 3 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1099 |  | HydraulicCircuit 3 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1100 |  | HydraulicCircuit 3 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1101 |  | HydraulicCircuit 3 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1102 |  | HydraulicCircuit 3 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1103 |  | HydraulicCircuit 3 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 1109 |  | HydraulicCircuit 4 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 1110 |  | HydraulicCircuit 4 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 1111 |  | HydraulicCircuit 4 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1112 |  | HydraulicCircuit 4 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1113 |  | HydraulicCircuit 4 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1114 |  | HydraulicCircuit 4 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1115 |  | HydraulicCircuit 4 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1116 |  | HydraulicCircuit 4 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 1122 |  | HydraulicCircuit 5 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 1123 |  | HydraulicCircuit 5 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 1124 |  | HydraulicCircuit 5 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1125 |  | HydraulicCircuit 5 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1126 |  | HydraulicCircuit 5 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1127 |  | HydraulicCircuit 5 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1128 |  | HydraulicCircuit 5 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1129 |  | HydraulicCircuit 5 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 1135 |  | HydraulicCircuit 6 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 1136 |  | HydraulicCircuit 6 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 1137 |  | HydraulicCircuit 6 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1138 |  | HydraulicCircuit 6 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1139 |  | HydraulicCircuit 6 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1140 |  | HydraulicCircuit 6 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1141 |  | HydraulicCircuit 6 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1142 |  | HydraulicCircuit 6 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 1148 |  | HydraulicCircuit 7 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 1149 |  | HydraulicCircuit 7 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 1150 |  | HydraulicCircuit 7 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1151 |  | HydraulicCircuit 7 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1152 |  | HydraulicCircuit 7 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1153 |  | HydraulicCircuit 7 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1154 |  | HydraulicCircuit 7 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1155 |  | HydraulicCircuit 7 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 1161 |  | HydraulicCircuit 8 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 1162 |  | HydraulicCircuit 8 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 1163 |  | HydraulicCircuit 8 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1164 |  | HydraulicCircuit 8 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1165 |  | HydraulicCircuit 8 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1166 |  | HydraulicCircuit 8 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1167 |  | HydraulicCircuit 8 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1168 |  | HydraulicCircuit 8 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 1201 |  | Heat Pump | Heat demand source | 0 | 2 | 0-Scheduler 1-System 2-Max_system_scheduler |  | int
HOLDING_REGISTER | Read | 1421 |  | Fresh Water Characteristics 3 | DHU Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 1422 |  | Fresh Water Characteristics 3 | Extra Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 1423 |  | Fresh Water Characteristics 3 | Maximum DHW Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 1424 |  | Fresh Water Characteristics 3 | On High Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 1425 |  | Fresh Water Characteristics 3 | On Low Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 1426 |  | Fresh Water Characteristics 3 | Fresh Water Type | 0 | 3 | 0-15/20l/min 1-27l/min 2-40l/min 3-60l/min |  | int
HOLDING_REGISTER | Read | 1427 |  | Fresh Water Characteristics 3 | Enable Alarm Output | 0 | 2 | 0-No 1-Yes 2-Inverted |  | int
HOLDING_REGISTER | Read | 1428 |  | Fresh Water Characteristics 3 | Buffer Cylinder Temperature Offset |  |  |  | K | int
HOLDING_REGISTER | Read | 1429 |  | Fresh Water Characteristics 3 | hrBitblock |  |  |  |  | int
| Read |  | 0 | Fresh Water | Buffer Cylinder Temperature Optimization Enabled |  |  |  |  | bit
| Read |  | 1 | Fresh Water | Impulse Enabled |  |  |  |  | bit
| Read |  | 2 | Fresh Water | Time Program Enabled |  |  |  |  | bit
HOLDING_REGISTER | Read | 1430 |  | Fresh Water Characteristics 3 | Minimum Buffer Cylinder Temperature Offset |  |  |  | K | int
HOLDING_REGISTER | Read | 1431 |  | Fresh Water Characteristics 2 | Circulation Pump Runs per Hour | 0 | 7 | 0-Undefined 1-1x3_minutes/h 2-2x3_minutes/h 3-3x3_minutes/h 4-4x3_minutes/h 5-5x3_minutes/h 6-6x3_minutes/h 7-Permanent |  | int
HOLDING_REGISTER | Read | 1432 |  | Fresh Water Characteristics 2 | Swich Hysteresis |  |  |  | K | int
HOLDING_REGISTER | Read | 1433 |  | Fresh Water Characteristics 2 | Thermal Disinfection Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 1434 |  | Fresh Water Characteristics 2 | Pre Heat Maximum Temperature |  |  |  | °C | int
INPUT_REGISTER | Read | 1000 |  | System | Own Outdoor temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1001 |  | System | Damped Own outdoor temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1004 |  | System | Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1008 |  | System | Active Functions 1 |  |  |  |  | int
INPUT_REGISTER | Read | 1009 |  | System | Active Functions 2 |  |  |  |  | int
INPUT_REGISTER | Read | 1015 |  | DomesticHotWater Zm | Charge Pump Running | 0 | 4 | 0-Stopping 1-Starting 2-Running 3-Off 4-Error |  | int
INPUT_REGISTER | Read | 1016 |  | DomesticHotWater Zm | Circulation Pump Running | 0 | 4 | 0-Stopping 1-Starting 2-Running 3-Off 4-Error |  | int
INPUT_REGISTER | Read | 1017 |  | DomesticHotWater Zm | Hydraulic State | 0 | 7 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Cold_load 6-Post_purge 7-Condense_protection |  | int
INPUT_REGISTER | Read | 1018 |  | DomesticHotWater Zm/Ems | Thermal Disinfection Status | 0 | 3 | 0-Off 1-On 2-Success 3-Error |  | int
INPUT_REGISTER | Read | 1019 |  | DomesticHotWater Zm/Ems | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 1020 |  | DomesticHotWater Zm/Ems | Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1021 |  | DomesticHotWater Zm/Ems | Current Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1031 |  | DomesticHotWater Fm | Charge Pump Running | 0 | 4 | 0-Stopping 1-Starting 2-Running 3-Off 4-Error |  | int
INPUT_REGISTER | Read | 1032 |  | DomesticHotWater Fm | Circulation Pump Running | 0 | 4 | 0-Stopping 1-Starting 2-Running 3-Off 4-Error |  | int
INPUT_REGISTER | Read | 1033 |  | DomesticHotWater Fm | Hydraulic State | 0 | 7 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Cold_load 6-Post_purge 7-Condense_protection |  | int
INPUT_REGISTER | Read | 1034 |  | DomesticHotWater Fm | Thermal Disinfection Status | 0 | 3 | 0-Off 1-On 2-Success 3-Error |  | int
INPUT_REGISTER | Read | 1035 |  | DomesticHotWater Fm | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 1036 |  | DomesticHotWater Fm | Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1037 |  | DomesticHotWater Fm | Current Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER |  | 1047 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 1048 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 1050 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 1052 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 1053 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 1054 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 1055 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 1056 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 1059 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 1060 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER | Read | 1063 |  | AlternativeHeatSource | Operating hours |  |  |  | h | long
INPUT_REGISTER | Read | 1065 |  | AlternativeHeatSource | Heat Source Starts |  |  |  |  | long
INPUT_REGISTER | Read | 1067 |  | AlternativeHeatSource | Heat Source Hours to Maintenance |  |  |  | h | int
INPUT_REGISTER | Read | 1069 |  | AlternativeHeatSource | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
| Read |  | 0 | AlternativeHeatSource | Is Heat Source On |  |  |  |  | bit
| Read |  | 1 | AlternativeHeatSource | Is Heat Source On Request |  |  |  |  | bit
INPUT_REGISTER | Read | 1087 |  | HydraulicCircuit Zm | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1088 |  | HydraulicCircuit Zm | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1089 |  | HydraulicCircuit Zm | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1090 |  | HydraulicCircuit Zm | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1091 |  | HydraulicCircuit Zm | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 1092 |  | HydraulicCircuit Zm | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 1093 |  | HydraulicCircuit Zm | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 1094 |  | HydraulicCircuit Zm | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 1095 |  | HydraulicCircuit Zm | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 1099 |  | HydraulicCircuit 1 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1100 |  | HydraulicCircuit 1 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1101 |  | HydraulicCircuit 1 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1102 |  | HydraulicCircuit 1 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1103 |  | HydraulicCircuit 1 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 1104 |  | HydraulicCircuit 1 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 1105 |  | HydraulicCircuit 1 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 1106 |  | HydraulicCircuit 1 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 1107 |  | HydraulicCircuit 1 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 1112 |  | HydraulicCircuit 2 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1113 |  | HydraulicCircuit 2 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1114 |  | HydraulicCircuit 2 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1115 |  | HydraulicCircuit 2 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1116 |  | HydraulicCircuit 2 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 1117 |  | HydraulicCircuit 2 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 1118 |  | HydraulicCircuit 2 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 1119 |  | HydraulicCircuit 2 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 1120 |  | HydraulicCircuit 2 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 1125 |  | HydraulicCircuit 3 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1126 |  | HydraulicCircuit 3 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1127 |  | HydraulicCircuit 3 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1128 |  | HydraulicCircuit 3 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1129 |  | HydraulicCircuit 3 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 1130 |  | HydraulicCircuit 3 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 1131 |  | HydraulicCircuit 3 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 1132 |  | HydraulicCircuit 3 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 1133 |  | HydraulicCircuit 3 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 1138 |  | HydraulicCircuit 4 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1139 |  | HydraulicCircuit 4 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1140 |  | HydraulicCircuit 4 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1141 |  | HydraulicCircuit 4 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1142 |  | HydraulicCircuit 4 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 1143 |  | HydraulicCircuit 4 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 1144 |  | HydraulicCircuit 4 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 1145 |  | HydraulicCircuit 4 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 1146 |  | HydraulicCircuit 4 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 1151 |  | HydraulicCircuit 5 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1152 |  | HydraulicCircuit 5 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1153 |  | HydraulicCircuit 5 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1154 |  | HydraulicCircuit 5 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1155 |  | HydraulicCircuit 5 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 1156 |  | HydraulicCircuit 5 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 1157 |  | HydraulicCircuit 5 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 1158 |  | HydraulicCircuit 5 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 1159 |  | HydraulicCircuit 5 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 1164 |  | HydraulicCircuit 6 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1165 |  | HydraulicCircuit 6 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1166 |  | HydraulicCircuit 6 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1167 |  | HydraulicCircuit 6 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1168 |  | HydraulicCircuit 6 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 1169 |  | HydraulicCircuit 6 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 1170 |  | HydraulicCircuit 6 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 1171 |  | HydraulicCircuit 6 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 1172 |  | HydraulicCircuit 6 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 1177 |  | HydraulicCircuit 7 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1178 |  | HydraulicCircuit 7 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1179 |  | HydraulicCircuit 7 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1180 |  | HydraulicCircuit 7 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1181 |  | HydraulicCircuit 7 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 1182 |  | HydraulicCircuit 7 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 1183 |  | HydraulicCircuit 7 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 1184 |  | HydraulicCircuit 7 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 1185 |  | HydraulicCircuit 7 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 1190 |  | HydraulicCircuit 8 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1191 |  | HydraulicCircuit 8 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1192 |  | HydraulicCircuit 8 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1193 |  | HydraulicCircuit 8 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1194 |  | HydraulicCircuit 8 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 1195 |  | HydraulicCircuit 8 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 1196 |  | HydraulicCircuit 8 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 1197 |  | HydraulicCircuit 8 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 1198 |  | HydraulicCircuit 8 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 1203 |  | i2c | Global Error State | 0 | 4 | 0-No_Error 1-i2c_driver_error 2-Wrong_Cycle_Time 3-Missing_Module_Slot 4-Module_Slot_Error |  | int
INPUT_REGISTER | Read | 1204 |  | i2c | Slot1 Module Detected |  |  | 0-Unknown 1-None 22-FM_CM 25-FM_SI 28-FM_MM 29-FM_MW 30-FM_AM 31-FM_CM2 |  | int
INPUT_REGISTER | Read | 1205 |  | i2c | Slot1 Error State |  |  | 0-No_Error 1-No_Response 2-Wrong_Module 3-Unsupported_Module 4-Internal_Sw_Error 5-Communication_Failed 6-Internal_Module_Error 7-Module_Not_Supported_Current_Variant 8-Module_Not_Suppported_In_Slot 9-Module_Count_Too_High 10-Module_Not_Supported_With_Connected_Boiler_Type |  | int
INPUT_REGISTER | Read | 1206 |  | i2c | Slot2 Module Detected |  |  | 0-Unknown 1-None 22-FM_CM 25-FM_SI 28-FM_MM 29-FM_MW 30-FM_AM 31-FM_CM2 |  | int
INPUT_REGISTER | Read | 1207 |  | i2c | Slot2 Error State |  |  | 0-No_Error 1-No_Response 2-Wrong_Module 3-Unsupported_Module 4-Internal_Sw_Error 5-Communication_Failed 6-Internal_Module_Error 7-Module_Not_Supported_Current_Variant 8-Module_Not_Suppported_In_Slot 9-Module_Count_Too_High 10-Module_Not_Supported_With_Connected_Boiler_Type |  | int
INPUT_REGISTER | Read | 1208 |  | i2c | Slot3 Module Detected |  |  | 0-Unknown 1-None 22-FM_CM 25-FM_SI 28-FM_MM 29-FM_MW 30-FM_AM 31-FM_CM2 |  | int
INPUT_REGISTER | Read | 1209 |  | i2c | Slot3 Error State |  |  | 0-No_Error 1-No_Response 2-Wrong_Module 3-Unsupported_Module 4-Internal_Sw_Error 5-Communication_Failed 6-Internal_Module_Error 7-Module_Not_Supported_Current_Variant 8-Module_Not_Suppported_In_Slot 9-Module_Count_Too_High 10-Module_Not_Supported_With_Connected_Boiler_Type |  | int
INPUT_REGISTER | Read | 1210 |  | i2c | Slot4 Module Detected |  |  | 0-Unknown 1-None 22-FM_CM 25-FM_SI 28-FM_MM 29-FM_MW 30-FM_AM 31-FM_CM2 |  | int
INPUT_REGISTER | Read | 1211 |  | i2c | Slot4 Error State |  |  | 0-No_Error 1-No_Response 2-Wrong_Module 3-Unsupported_Module 4-Internal_Sw_Error 5-Communication_Failed 6-Internal_Module_Error 7-Module_Not_Supported_Current_Variant 8-Module_Not_Suppported_In_Slot 9-Module_Count_Too_High 10-Module_Not_Supported_With_Connected_Boiler_Type |  | int
INPUT_REGISTER | Read | 1212 |  | i2c | Slot A Module Detected |  |  | 0-Unknown 1-None 26-ZM5313 27-ZM5311 |  | int
INPUT_REGISTER | Read | 1213 |  | i2c | Slot A Error State |  |  | 0-No_Error 1-No_Response 2-Wrong_Module 3-Unsupported_Module 4-Internal_Sw_Error 5-Communication_Failed 6-Internal_Module_Error 7-Module_Not_Supported_Current_Variant 8-Module_Not_Suppported_In_Slot 9-Module_Count_Too_High 10-Module_Not_Supported_With_Connected_Boiler_Type |  | int
INPUT_REGISTER | Read | 1214 |  | i2c | irBitblock |  |  |  |  | int
| Read |  | 0 | i2c | Component Error |  |  |  |  | bit
INPUT_REGISTER | Read | 1225 |  | fm-si | irBitblock |  |  |  |  | int
| Read |  | 0 | fm-si | Input 1 Error |  |  |  |  | bit
| Read |  | 1 | fm-si | Input 2 Error |  |  |  |  | bit
| Read |  | 2 | fm-si | Input 3 Error |  |  |  |  | bit
| Read |  | 3 | fm-si | Input 4 Error |  |  |  |  | bit
| Read |  | 4 | fm-si | Input 5 Error |  |  |  |  | bit
INPUT_REGISTER | Read | 1232 |  | Sdc | Demand Mode (Low Priority) | 0 | 2 | 0-Off 1-Take_Heat 2-Give_Heat |  | int
INPUT_REGISTER | Read | 1233 |  | Sdc | Demand Flow Temp (Low Priority) |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1234 |  | Sdc | Demand Mode (High Priority) | 0 | 2 | 0-Off 1-Take_Heat 2-Give_Heat |  | int
INPUT_REGISTER | Read | 1235 |  | Sdc | Demand Flow Temp (High Priority) |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1239 |  | Heat Pump | System return temperature for HP heating buffer |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1240 |  | Heat Pump | Buffer mid temperature for HP heating buffer |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1241 |  | Heat Pump | Buffer top temperature for HP heating buffer |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1242 |  | Heat Pump | Buffer bottom temperature for HP heating buffer |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1243 |  | Heat Pump | Return temperature FWR |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1244 |  | Heat Pump | Flow temperature FWV |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1245 |  | Heat Pump | Flow temperature HP |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1246 |  | Heat Pump | Return temperature HP |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1247 |  | Heat Pump | HMI State of HP Component | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 1248 |  | Heat Pump | HP current heat output |  |  |  | kW | signed int | x10
INPUT_REGISTER | Read | 1249 |  | Heat Pump | HP current electrical power consumption | 0 | 10000 |  | kW | int | x10
INPUT_REGISTER | Read | 1250 |  | Heat Pump | HP Smart grid mode | 0 | 3 | 0-normal_charging_grid 1-low_charging_grid 2-high_charging_grid 3-free_charging_grid |  | int
INPUT_REGISTER | Read | 1251 |  | Heat Pump | Heat demand temperature set point |  |  |  | °C | int
INPUT_REGISTER | Read | 1252 |  | Heat Pump | heatPumpStatusIrBitblock | 0 |  |  |  | int
INPUT_REGISTER | Read | 1253 |  | Heat Pump | Ambient Temperature HP |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1254 |  | Heat Pump | HP silent mode | 0 | 3 | 0-standard_mode 1-silent_mode 2-super_silent_mode 3-night_mode |  | int
INPUT_REGISTER | Read | 1255 |  | Heat Pump | Heat Pump Heat Request Temperature |  |  |  | °C | int
INPUT_REGISTER | Read | 1256 |  | Heat Pump | heatPumpIrBitblock |  |  |  |  | int
INPUT_REGISTER | Read | 1265 |  | System | Open Notifications Count |  |  |  |  | int
INPUT_REGISTER | Read | 1266 |  | System | Error Key 5 |  |  |  |  | long
INPUT_REGISTER | Read | 1268 |  | System | Error Key 6 |  |  |  |  | long
INPUT_REGISTER | Read | 1270 |  | System | Error Key 7 |  |  |  |  | long
INPUT_REGISTER | Read | 1272 |  | System | Error Key 8 |  |  |  |  | long
INPUT_REGISTER | Read | 1274 |  | System | Error Key 9 |  |  |  |  | long
INPUT_REGISTER | Read | 1276 |  | System | Error Key 10 |  |  |  |  | long
INPUT_REGISTER | Read | 1278 |  | Chp / EC Power | Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1279 |  | Chp / EC Power | Return Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1280 |  | Chp | Flue Gas Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1281 |  | Chp | Motor Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1282 |  | Chp / EC Power | Current Generator Power |  |  |  | kW | int
INPUT_REGISTER | Read | 1283 |  | Chp | Current Power Setpoint |  |  |  | kW | int
INPUT_REGISTER | Read | 1284 |  | Chp / EC Power | Operation Hours |  |  |  | h | long
INPUT_REGISTER | Read | 1286 |  | Chp / EC Power | Number of starts |  |  |  |  | long
INPUT_REGISTER | Read | 1288 |  | Chp / EC Power | Hours to Maintenance |  |  |  | h | int
INPUT_REGISTER | Read | 1290 |  | Chp | Output Power Setpoint |  |  |  | kW | int
INPUT_REGISTER | Read | 1291 |  | Chp | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 1296 |  | Chp | irBitblock |  |  |  |  | int
| Read |  | 0 | Chp | Warning |  |  |  |  | bit
| Read |  | 1 | Chp / EC Power | Malfunction |  |  |  |  | bit
| Read |  | 2 | Chp / EC Power | Controlled Shutdown |  |  |  |  | bit
| Read |  | 3 | Chp / EC Power | Generator On |  |  |  |  | bit
| Read |  | 4 | Chp | Automatic On |  |  |  |  | bit
| Read |  | 5 | Chp / EC Power | Automatic Ready |  |  |  |  | bit
| Read |  | 11 | Chp / EC Power | Output On Request |  |  |  |  | bit
INPUT_REGISTER | Read | 1304 |  | Water Treatment Module | Program Step |  |  | 20-140: Desalination not active 10000-10810: One time desalination 20000-20810: Automatic desalination 30000-30260: Stationary operation |  | int
INPUT_REGISTER | Read | 1305 |  | Water Treatment Module | Temperature Desalinization |  |  |  | °C | int | x10
INPUT_REGISTER | Read | 1306 |  | Water Treatment Module | Volume Flow |  |  |  | L/min | int | x10
INPUT_REGISTER | Read | 1307 |  | Water Treatment Module | Conductivity system |  |  |  | uS/cm | int | x10
INPUT_REGISTER | Read | 1308 |  | Water Treatment Module | Conductivity cartridge |  |  |  | uS/cm | int | x10
INPUT_REGISTER | Read | 1309 |  | Water Treatment Module | Cartridge Capacity |  |  |  | % | int
INPUT_REGISTER | Read | 1313 |  | Solar Data | Collector temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1314 |  | Solar Data | Temperature cylinder bottom |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1315 |  | Solar Data | Solar pump modulation setpoint |  |  |  | % | int
INPUT_REGISTER | Read | 1316 |  | Solar | Solar pump status | 0 | 19 | 1-TestMod 2-BlckProt 3-No heat 4-Ht avail 5-SolOff 6-MaxCyl 7-MaxColl 8-MinColl 9-FrostP 10-VacFct 11-SwChck 12-MixPrio 13-Switch 14-Priority 15-ThermD 16-MixCal 17-MixOpn 18-MixCl 19-MixOff |  | int
INPUT_REGISTER | Read | 1317 |  | Solar Data | Heat exchanger temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1318 |  | Solar Data | Heat exchanger pump modulation setpoint |  |  |  | % | int
INPUT_REGISTER | Read | 1319 |  | Solar | Heat exchanger pump status | 0 | 19 | 1-TestMod 2-BlckProt 3-No heat 4-Ht avail 5-SolOff 6-MaxCyl 7-MaxColl 8-MinColl 9-FrostP 10-VacFct 11-SwChck 12-MixPrio 13-Switch 14-Priority 15-ThermD 16-MixCal 17-MixOpn 18-MixCl 19-MixOff |  | int
INPUT_REGISTER | Read | 1320 |  | Solar Data | Temperature cylinder 3 top |  |  |  | °C | int | x10
INPUT_REGISTER | Read | 1321 |  | Solar Data | Reload pump modulation setpoint |  |  |  | % | int
INPUT_REGISTER | Read | 1322 |  | Solar | Reload pump status | 0 | 19 | 1-TestMod 2-BlckProt 3-No heat 4-Ht avail 5-SolOff 6-MaxCyl 7-MaxColl 8-MinColl 9-FrostP 10-VacFct 11-SwChck 12-MixPrio 13-Switch 14-Priority 15-ThermD 16-MixCal 17-MixOpn 18-MixCl 19-MixOff |  | int
INPUT_REGISTER | Read | 1323 |  | Solar | Pump therm. disinfect. status | 0 | 19 | 1-TestMod 2-BlckProt 3-No heat 4-Ht avail 5-SolOff 6-MaxCyl 7-MaxColl 8-MinColl 9-FrostP 10-VacFct 11-SwChck 12-MixPrio 13-Switch 14-Priority 15-ThermD 16-MixCal 17-MixOpn 18-MixCl 19-MixOff |  | int
INPUT_REGISTER | Read | 1324 |  | Solar Yield | Flow temperature heat meter |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1325 |  | Solar Yield | Return temperature heat meter |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1326 |  | Solar Yield | Heat count pulse counter | 0 | 15 |  |  | int
INPUT_REGISTER | Read | 1327 |  | Solar Yield | Solar yield per month |  |  |  | kWh | long | x10
INPUT_REGISTER | Read | 1329 |  | Solar Yield | Solar yield per year |  |  |  | kWh | long | x10
INPUT_REGISTER | Read | 1331 |  | Solar Yield | Last hour solar yield |  |  |  | kWh | long | x10
INPUT_REGISTER | Read | 1333 |  | Solar Yield | Solar yield per day |  |  |  | kWh | long | x10
INPUT_REGISTER | Read | 1335 |  | Solar Yield | Solar yield since installation |  |  |  | kWh | long | x10
INPUT_REGISTER | Read | 1337 |  | Solar | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 1338 |  | Solar Data | Hydraulic configuration |  |  |  |  | int
| Read |  | 0 | Solar | Option 1 active |  |  |  |  | bit
| Read |  | 1 | Solar | Option A active |  |  |  |  | bit
| Read |  | 2 | Solar | Option B active |  |  |  |  | bit
| Read |  | 3 | Solar | Option C active |  |  |  |  | bit
| Read |  | 4 | Solar | Option D active |  |  |  |  | bit
| Read |  | 5 | Solar | Option E active |  |  |  |  | bit
| Read |  | 6 | Solar | Option F active |  |  |  |  | bit
| Read |  | 7 | Solar | Option G active |  |  |  |  | bit
| Read |  | 8 | Solar | Option H active |  |  |  |  | bit
| Read |  | 9 | Solar | Option I active |  |  |  |  | bit
| Read |  | 10 | Solar | Option J active |  |  |  |  | bit
| Read |  | 11 | Solar | Option K active |  |  |  |  | bit
| Read |  | 12 | Solar | Option L active |  |  |  |  | bit
| Read |  | 13 | Solar | Option M active |  |  |  |  | bit
| Read |  | 14 | Solar | Option N active |  |  |  |  | bit
| Read |  | 15 | Solar | Option P active |  |  |  |  | bit
INPUT_REGISTER | Read | 1339 |  | Solar Data | irBitblock |  |  |  |  | int
| Read |  | 0 | Solar | Is Active |  |  |  |  | bit
INPUT_REGISTER |  | 1400 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 1401 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 1402 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 1403 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 1404 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 1405 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 1406 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 1407 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 1408 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 1409 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 1410 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 1411 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 1412 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 1413 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER | Read | 1422 |  | Energy Monitoring | Heat Output |  |  |  | kW | signed int | x10
INPUT_REGISTER | Read | 1423 |  | Energy Monitoring | Gas Consumption (LCV) |  |  |  | kW | signed int | x10
INPUT_REGISTER | Read | 1425 |  | Energy Monitoring | Electrical Power |  |  |  | W | int
INPUT_REGISTER | Read | 1430 |  | Fresh Water Characteristics 1 | DHW Out Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1431 |  | Fresh Water Characteristics 1 | DHW Volume Flow |  |  |  | L/min | signed int | x10
INPUT_REGISTER | Read | 1432 |  | Fresh Water Characteristics 1 | Prim In Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1433 |  | Fresh Water Characteristics 1 | DHW In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1434 |  | Fresh Water Characteristics 1 | Primary Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 1435 |  | Fresh Water Characteristics 1 | Request DHW Out Temperature |  |  |  | °C | int
INPUT_REGISTER | Read | 1436 |  | Fresh Water Characteristics 1 | Status Request DHW Out Temperature | 0 | 9 | 0-Off 1-DHWRed 2-DHW 3-Sol_red 4-Once_on 5-Therm_d 6-DlyHtUp 7-Preheat_start 8-Preheat_normal 9-No_eq |  | int
INPUT_REGISTER | Read | 1437 |  | Fresh Water Characteristics 2 | Circulation Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 1438 |  | Fresh Water Characteristics 2 | Status Circulation Pump | 0 | 8 | 0-Undefined 1-Test 2-BlckProt 3-No_req 4-AutoOff 5-AutoOn 6-Therm_d 7-Sys_Off 8-DlyHtUp |  | int
INPUT_REGISTER | Read | 1439 |  | Fresh Water Characteristics 2 | Return Valve Modulation Request |  |  |  | % | int
INPUT_REGISTER | Read | 1440 |  | Fresh Water Characteristics 2 | Valve State | 0 | 5 | 0-Undefined 1-TestMod 2-BlckProt 3-Mix_cl 4-Mix_opn 5-Sys_Off |  | int
INPUT_REGISTER | Read | 1441 |  | Fresh Water Characteristics 2 | Return Valve Buffer Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1442 |  | Fresh Water Characteristics 2 | Disinfection Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 1443 |  | Fresh Water Characteristics 2 | Pump State | 0 | 5 | 0-Undefined 1-TestMod 2-BlckPro 3-No_eq 4-Ht_req 5-Sys_Off |  | int
INPUT_REGISTER | Read | 1444 |  | Fresh Water Characteristics 1 | DHW Valve Power |  |  |  | % | int
INPUT_REGISTER | Read | 1445 |  | Fresh Water Characteristics 2 | Total Flow |  |  |  | L/min | int | x10
INPUT_REGISTER | Read | 1446 |  | Fresh Water 2 | Module 2 DHW Out Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1447 |  | Fresh Water 2 | Module 2 DHW Volume Flow |  |  |  | L/min | signed int | x10
INPUT_REGISTER | Read | 1448 |  | Fresh Water 2 | Module 2 Prim In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1449 |  | Fresh Water 2 | Module 2 DHW In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1450 |  | Fresh Water 2 | Module 2 DHW Valve Power |  |  |  | % | int
INPUT_REGISTER | Read | 1451 |  | Fresh Water 2 | Module 2 Prim Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 1452 |  | Fresh Water 2 | Module 2 Status Prim Pump |  |  |  |  | int
INPUT_REGISTER | Read | 1453 |  | Fresh Water 3 | Module 3 DHW Out Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1454 |  | Fresh Water 3 | Module 3 DHW Volume Flow |  |  |  | L/min | signed int | x10
INPUT_REGISTER | Read | 1455 |  | Fresh Water 3 | Module 3 Prim In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1456 |  | Fresh Water 3 | Module 3 DHW In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1457 |  | Fresh Water 3 | Module 3 DHW Valve Power |  |  |  | % | int
INPUT_REGISTER | Read | 1458 |  | Fresh Water 3 | Module 3 Prim Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 1459 |  | Fresh Water 3 | Module 3 Status Prim Pump |  |  |  |  | int
INPUT_REGISTER | Read | 1460 |  | Fresh Water 4 | Module 4 DHW Out Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1461 |  | Fresh Water 4 | Module 4 DHW Volume Flow |  |  |  | L/min | signed int | x10
INPUT_REGISTER | Read | 1462 |  | Fresh Water 4 | Module 4 Prim In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1463 |  | Fresh Water 4 | Module 4 DHW In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1464 |  | Fresh Water 4 | Module 4 DHW ValvePower |  |  |  | % | int
INPUT_REGISTER | Read | 1465 |  | Fresh Water 4 | Module 4 Prim Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 1466 |  | Fresh Water 4 | Module 4 Status Primary Pump |  |  |  |  | int
INPUT_REGISTER | Read | 1467 |  | Fresh Water | Fresh Water Hmi State |  |  |  |  | int
INPUT_REGISTER | Read | 1468 |  | Fresh Water Characteristics 3 | Fresh Water Configurations |  |  |  |  | int
| Read |  | 0 | Fresh Water | Option 2 active |  |  |  |  | bit
| Read |  | 1 | Fresh Water | Option A active |  |  |  |  | bit
| Read |  | 2 | Fresh Water | Option B active |  |  |  |  | bit
| Read |  | 3 | Fresh Water | Option C active |  |  |  |  | bit
| Read |  | 4 | Fresh Water | Option D active |  |  |  |  | bit
| Read |  | 5 | Fresh Water | Option E active |  |  |  |  | bit
| Read |  | 6 | Fresh Water | Option E active cascade module 2 active |  |  |  |  | bit
| Read |  | 7 | Fresh Water | Option E active cascade module 3 active |  |  |  |  | bit
| Read |  | 8 | Fresh Water | Option E active cascade module 4 active |  |  |  |  | bit
| Read |  | 9 | Fresh Water | Is Active |  |  |  |  | bit
INPUT_REGISTER | Read | 1476 |  | System | Error Key 1 |  |  |  |  | long
INPUT_REGISTER | Read | 1478 |  | System | Error Key 2 |  |  |  |  | long
INPUT_REGISTER | Read | 1480 |  | System | Error Key 3 |  |  |  |  | long
INPUT_REGISTER | Read | 1482 |  | System | Error Key 4 |  |  |  |  | long
INPUT_REGISTER | Read | 1484 |  | System | Error 1 Extra Info (MSB) |  |  |  |  | long
INPUT_REGISTER | Read | 1486 |  | System | Error 1 Extra Info (LSB) |  |  |  |  | long
INPUT_REGISTER | Read | 1488 |  | System | Error 2 Extra Info (MSB) |  |  |  |  | long
INPUT_REGISTER | Read | 1490 |  | System | Error 2 Extra Info (LSB) |  |  |  |  | long
INPUT_REGISTER | Read | 1492 |  | System | Error 3 Extra Info (MSB) |  |  |  |  | long
INPUT_REGISTER | Read | 1494 |  | System | Error 3 Extra Info (LSB) |  |  |  |  | long
INPUT_REGISTER | Read | 1496 |  | System | Error 4 Extra Info (MSB) |  |  |  |  | long
INPUT_REGISTER | Read | 1498 |  | System | Error 4 Extra Info (LSB) |  |  |  |  | long

## Slave03
Register Type | Permissions | Address | Bitblock Bit | Component | Name | Min | Max | Range | Unit | DataType | Float to Int Factor
HOLDING_REGISTER | Write | 1507 |  | DomesticHotWater Zm/Ems | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 1508 |  | DomesticHotWater Zm/Ems | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 1509 |  | DomesticHotWater Zm/Ems | Thermal Disinfection Setpoint | 65 | 75 |  | °C | int | x10
HOLDING_REGISTER | Write | 1510 |  | DomesticHotWater Zm | Setpoint Auto Day | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 1511 |  | DomesticHotWater Zm | Setpoint Auto Night | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 1512 |  | DomesticHotWater Zm | Setpoint Manual Day | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 1513 |  | DomesticHotWater Zm | Setpoint Manual Night | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 1514 |  | DomesticHotWater Zm | Setpoint Holiday | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 1515 |  | DomesticHotWater Zm/Ems | Circulation Pump Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 1516 |  | DomesticHotWater Zm/Ems | Circulation Pump Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 1517 |  | DomesticHotWater Zm/Ems | Disinfection Frequency | 0 | 7 | 0-Daily 1-Monday 2-Tuesday 3-Wednesday 4-Thursday 5-Friday 6-Saturday 7-Sunday |  | int
HOLDING_REGISTER | Write | 1518 |  | DomesticHotWater Zm/Ems | Disinfection Start Hour | 0 | 23 |  | h | int
HOLDING_REGISTER | Write | 1521 |  | DomesticHotWater Fm | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 1522 |  | DomesticHotWater Fm | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 1523 |  | DomesticHotWater Fm | Thermal Disinfection Setpoint | 65 | 75 |  | °C | int | x10
HOLDING_REGISTER | Write | 1524 |  | DomesticHotWater Fm | Setpoint Auto Day | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 1525 |  | DomesticHotWater Fm | Setpoint Auto Night | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 1526 |  | DomesticHotWater Fm | Setpoint Manual Day | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 1527 |  | DomesticHotWater Fm | Setpoint Manual Night | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 1528 |  | DomesticHotWater Fm | Setpoint Holiday | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 1529 |  | DomesticHotWater Fm | Circulation Pump Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 1530 |  | DomesticHotWater Fm | Circulation Pump Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 1531 |  | DomesticHotWater Fm | Disinfection Frequency | 0 | 7 | 0-Daily 1-Monday 2-Tuesday 3-Wednesday 4-Thursday 5-Friday 6-Saturday 7-Sunday |  | int
HOLDING_REGISTER | Write | 1532 |  | DomesticHotWater Fm | Disinfection Start Hour | 0 | 23 |  | h | int
HOLDING_REGISTER | Read | 1539 |  | Boiler | Control Type | 0 | 4 | 0-None 1-Safe 2-Ems 3-7Pole 4-Substation |  | int
HOLDING_REGISTER | Write | 1543 |  | AlternativeHeatSource | Operation Mode Request Auto Day | 20 | 99 |  | °C | int
HOLDING_REGISTER | Write | 1544 |  | AlternativeHeatSource | Operation Mode Request Auto Night | 20 | 99 |  | °C | int
HOLDING_REGISTER | Write | 1545 |  | AlternativeHeatSource | Operation Mode Request Manual Day | 20 | 99 |  | °C | int
HOLDING_REGISTER | Write | 1546 |  | AlternativeHeatSource | Operation Mode Request Manual Night | 20 | 99 |  | °C | int
HOLDING_REGISTER | Write | 1547 |  | AlternativeHeatSource | Operation Mode Request Holiday | 20 | 99 |  | °C | int
HOLDING_REGISTER | Write | 1548 |  | AlternativeHeatSource | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 1549 |  | AlternativeHeatSource | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 1550 |  | AlternativeHeatSource | Return Control Setpoint User | 10 | 70 |  | °C | int
HOLDING_REGISTER | Write | 1557 |  | HydraulicCircuit Zm | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 1558 |  | HydraulicCircuit Zm | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 1559 |  | HydraulicCircuit Zm | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1560 |  | HydraulicCircuit Zm | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1561 |  | HydraulicCircuit Zm | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1562 |  | HydraulicCircuit Zm | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1563 |  | HydraulicCircuit Zm | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1564 |  | HydraulicCircuit Zm | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 1570 |  | HydraulicCircuit 1 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 1571 |  | HydraulicCircuit 1 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 1572 |  | HydraulicCircuit 1 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1573 |  | HydraulicCircuit 1 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1574 |  | HydraulicCircuit 1 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1575 |  | HydraulicCircuit 1 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1576 |  | HydraulicCircuit 1 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1577 |  | HydraulicCircuit 1 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 1583 |  | HydraulicCircuit 2 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 1584 |  | HydraulicCircuit 2 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 1585 |  | HydraulicCircuit 2 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1586 |  | HydraulicCircuit 2 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1587 |  | HydraulicCircuit 2 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1588 |  | HydraulicCircuit 2 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1589 |  | HydraulicCircuit 2 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1590 |  | HydraulicCircuit 2 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 1596 |  | HydraulicCircuit 3 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 1597 |  | HydraulicCircuit 3 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 1598 |  | HydraulicCircuit 3 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1599 |  | HydraulicCircuit 3 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1600 |  | HydraulicCircuit 3 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1601 |  | HydraulicCircuit 3 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1602 |  | HydraulicCircuit 3 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1603 |  | HydraulicCircuit 3 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 1609 |  | HydraulicCircuit 4 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 1610 |  | HydraulicCircuit 4 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 1611 |  | HydraulicCircuit 4 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1612 |  | HydraulicCircuit 4 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1613 |  | HydraulicCircuit 4 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1614 |  | HydraulicCircuit 4 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1615 |  | HydraulicCircuit 4 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1616 |  | HydraulicCircuit 4 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 1622 |  | HydraulicCircuit 5 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 1623 |  | HydraulicCircuit 5 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 1624 |  | HydraulicCircuit 5 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1625 |  | HydraulicCircuit 5 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1626 |  | HydraulicCircuit 5 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1627 |  | HydraulicCircuit 5 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1628 |  | HydraulicCircuit 5 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1629 |  | HydraulicCircuit 5 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 1635 |  | HydraulicCircuit 6 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 1636 |  | HydraulicCircuit 6 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 1637 |  | HydraulicCircuit 6 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1638 |  | HydraulicCircuit 6 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1639 |  | HydraulicCircuit 6 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1640 |  | HydraulicCircuit 6 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1641 |  | HydraulicCircuit 6 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1642 |  | HydraulicCircuit 6 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 1648 |  | HydraulicCircuit 7 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 1649 |  | HydraulicCircuit 7 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 1650 |  | HydraulicCircuit 7 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1651 |  | HydraulicCircuit 7 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1652 |  | HydraulicCircuit 7 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1653 |  | HydraulicCircuit 7 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1654 |  | HydraulicCircuit 7 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1655 |  | HydraulicCircuit 7 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 1661 |  | HydraulicCircuit 8 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 1662 |  | HydraulicCircuit 8 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 1663 |  | HydraulicCircuit 8 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1664 |  | HydraulicCircuit 8 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1665 |  | HydraulicCircuit 8 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1666 |  | HydraulicCircuit 8 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1667 |  | HydraulicCircuit 8 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 1668 |  | HydraulicCircuit 8 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 1701 |  | Heat Pump | Heat demand source | 0 | 2 | 0-Scheduler 1-System 2-Max_system_scheduler |  | int
HOLDING_REGISTER | Read | 1921 |  | Fresh Water Characteristics 3 | DHU Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 1922 |  | Fresh Water Characteristics 3 | Extra Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 1923 |  | Fresh Water Characteristics 3 | Maximum DHW Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 1924 |  | Fresh Water Characteristics 3 | On High Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 1925 |  | Fresh Water Characteristics 3 | On Low Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 1926 |  | Fresh Water Characteristics 3 | Fresh Water Type | 0 | 3 | 0-15/20l/min 1-27l/min 2-40l/min 3-60l/min |  | int
HOLDING_REGISTER | Read | 1927 |  | Fresh Water Characteristics 3 | Enable Alarm Output | 0 | 2 | 0-No 1-Yes 2-Inverted |  | int
HOLDING_REGISTER | Read | 1928 |  | Fresh Water Characteristics 3 | Buffer Cylinder Temperature Offset |  |  |  | K | int
HOLDING_REGISTER | Read | 1929 |  | Fresh Water Characteristics 3 | hrBitblock |  |  |  |  | int
| Read |  | 0 | Fresh Water | Buffer Cylinder Temperature Optimization Enabled |  |  |  |  | bit
| Read |  | 1 | Fresh Water | Impulse Enabled |  |  |  |  | bit
| Read |  | 2 | Fresh Water | Time Program Enabled |  |  |  |  | bit
HOLDING_REGISTER | Read | 1930 |  | Fresh Water Characteristics 3 | Minimum Buffer Cylinder Temperature Offset |  |  |  | K | int
HOLDING_REGISTER | Read | 1931 |  | Fresh Water Characteristics 2 | Circulation Pump Runs per Hour | 0 | 7 | 0-Undefined 1-1x3_minutes/h 2-2x3_minutes/h 3-3x3_minutes/h 4-4x3_minutes/h 5-5x3_minutes/h 6-6x3_minutes/h 7-Permanent |  | int
HOLDING_REGISTER | Read | 1932 |  | Fresh Water Characteristics 2 | Swich Hysteresis |  |  |  | K | int
HOLDING_REGISTER | Read | 1933 |  | Fresh Water Characteristics 2 | Thermal Disinfection Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 1934 |  | Fresh Water Characteristics 2 | Pre Heat Maximum Temperature |  |  |  | °C | int
INPUT_REGISTER | Read | 1500 |  | System | Own Outdoor temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1501 |  | System | Damped Own outdoor temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1504 |  | System | Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1508 |  | System | Active Functions 1 |  |  |  |  | int
INPUT_REGISTER | Read | 1509 |  | System | Active Functions 2 |  |  |  |  | int
INPUT_REGISTER | Read | 1515 |  | DomesticHotWater Zm | Charge Pump Running | 0 | 4 | 0-Stopping 1-Starting 2-Running 3-Off 4-Error |  | int
INPUT_REGISTER | Read | 1516 |  | DomesticHotWater Zm | Circulation Pump Running | 0 | 4 | 0-Stopping 1-Starting 2-Running 3-Off 4-Error |  | int
INPUT_REGISTER | Read | 1517 |  | DomesticHotWater Zm | Hydraulic State | 0 | 7 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Cold_load 6-Post_purge 7-Condense_protection |  | int
INPUT_REGISTER | Read | 1518 |  | DomesticHotWater Zm/Ems | Thermal Disinfection Status | 0 | 3 | 0-Off 1-On 2-Success 3-Error |  | int
INPUT_REGISTER | Read | 1519 |  | DomesticHotWater Zm/Ems | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 1520 |  | DomesticHotWater Zm/Ems | Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1521 |  | DomesticHotWater Zm/Ems | Current Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1531 |  | DomesticHotWater Fm | Charge Pump Running | 0 | 4 | 0-Stopping 1-Starting 2-Running 3-Off 4-Error |  | int
INPUT_REGISTER | Read | 1532 |  | DomesticHotWater Fm | Circulation Pump Running | 0 | 4 | 0-Stopping 1-Starting 2-Running 3-Off 4-Error |  | int
INPUT_REGISTER | Read | 1533 |  | DomesticHotWater Fm | Hydraulic State | 0 | 7 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Cold_load 6-Post_purge 7-Condense_protection |  | int
INPUT_REGISTER | Read | 1534 |  | DomesticHotWater Fm | Thermal Disinfection Status | 0 | 3 | 0-Off 1-On 2-Success 3-Error |  | int
INPUT_REGISTER | Read | 1535 |  | DomesticHotWater Fm | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 1536 |  | DomesticHotWater Fm | Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1537 |  | DomesticHotWater Fm | Current Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER |  | 1547 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 1548 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 1550 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 1552 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 1553 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 1554 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 1555 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 1556 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 1559 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 1560 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER | Read | 1563 |  | AlternativeHeatSource | Operating hours |  |  |  | h | long
INPUT_REGISTER | Read | 1565 |  | AlternativeHeatSource | Heat Source Starts |  |  |  |  | long
INPUT_REGISTER | Read | 1567 |  | AlternativeHeatSource | Heat Source Hours to Maintenance |  |  |  | h | int
INPUT_REGISTER | Read | 1569 |  | AlternativeHeatSource | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
| Read |  | 0 | AlternativeHeatSource | Is Heat Source On |  |  |  |  | bit
| Read |  | 1 | AlternativeHeatSource | Is Heat Source On Request |  |  |  |  | bit
INPUT_REGISTER | Read | 1587 |  | HydraulicCircuit Zm | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1588 |  | HydraulicCircuit Zm | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1589 |  | HydraulicCircuit Zm | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1590 |  | HydraulicCircuit Zm | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1591 |  | HydraulicCircuit Zm | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 1592 |  | HydraulicCircuit Zm | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 1593 |  | HydraulicCircuit Zm | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 1594 |  | HydraulicCircuit Zm | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 1595 |  | HydraulicCircuit Zm | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 1599 |  | HydraulicCircuit 1 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1600 |  | HydraulicCircuit 1 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1601 |  | HydraulicCircuit 1 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1602 |  | HydraulicCircuit 1 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1603 |  | HydraulicCircuit 1 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 1604 |  | HydraulicCircuit 1 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 1605 |  | HydraulicCircuit 1 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 1606 |  | HydraulicCircuit 1 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 1607 |  | HydraulicCircuit 1 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 1612 |  | HydraulicCircuit 2 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1613 |  | HydraulicCircuit 2 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1614 |  | HydraulicCircuit 2 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1615 |  | HydraulicCircuit 2 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1616 |  | HydraulicCircuit 2 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 1617 |  | HydraulicCircuit 2 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 1618 |  | HydraulicCircuit 2 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 1619 |  | HydraulicCircuit 2 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 1620 |  | HydraulicCircuit 2 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 1625 |  | HydraulicCircuit 3 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1626 |  | HydraulicCircuit 3 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1627 |  | HydraulicCircuit 3 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1628 |  | HydraulicCircuit 3 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1629 |  | HydraulicCircuit 3 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 1630 |  | HydraulicCircuit 3 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 1631 |  | HydraulicCircuit 3 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 1632 |  | HydraulicCircuit 3 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 1633 |  | HydraulicCircuit 3 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 1638 |  | HydraulicCircuit 4 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1639 |  | HydraulicCircuit 4 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1640 |  | HydraulicCircuit 4 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1641 |  | HydraulicCircuit 4 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1642 |  | HydraulicCircuit 4 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 1643 |  | HydraulicCircuit 4 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 1644 |  | HydraulicCircuit 4 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 1645 |  | HydraulicCircuit 4 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 1646 |  | HydraulicCircuit 4 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 1651 |  | HydraulicCircuit 5 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1652 |  | HydraulicCircuit 5 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1653 |  | HydraulicCircuit 5 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1654 |  | HydraulicCircuit 5 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1655 |  | HydraulicCircuit 5 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 1656 |  | HydraulicCircuit 5 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 1657 |  | HydraulicCircuit 5 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 1658 |  | HydraulicCircuit 5 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 1659 |  | HydraulicCircuit 5 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 1664 |  | HydraulicCircuit 6 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1665 |  | HydraulicCircuit 6 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1666 |  | HydraulicCircuit 6 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1667 |  | HydraulicCircuit 6 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1668 |  | HydraulicCircuit 6 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 1669 |  | HydraulicCircuit 6 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 1670 |  | HydraulicCircuit 6 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 1671 |  | HydraulicCircuit 6 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 1672 |  | HydraulicCircuit 6 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 1677 |  | HydraulicCircuit 7 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1678 |  | HydraulicCircuit 7 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1679 |  | HydraulicCircuit 7 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1680 |  | HydraulicCircuit 7 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1681 |  | HydraulicCircuit 7 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 1682 |  | HydraulicCircuit 7 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 1683 |  | HydraulicCircuit 7 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 1684 |  | HydraulicCircuit 7 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 1685 |  | HydraulicCircuit 7 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 1690 |  | HydraulicCircuit 8 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1691 |  | HydraulicCircuit 8 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1692 |  | HydraulicCircuit 8 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1693 |  | HydraulicCircuit 8 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1694 |  | HydraulicCircuit 8 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 1695 |  | HydraulicCircuit 8 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 1696 |  | HydraulicCircuit 8 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 1697 |  | HydraulicCircuit 8 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 1698 |  | HydraulicCircuit 8 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 1703 |  | i2c | Global Error State | 0 | 4 | 0-No_Error 1-i2c_driver_error 2-Wrong_Cycle_Time 3-Missing_Module_Slot 4-Module_Slot_Error |  | int
INPUT_REGISTER | Read | 1704 |  | i2c | Slot1 Module Detected |  |  | 0-Unknown 1-None 22-FM_CM 25-FM_SI 28-FM_MM 29-FM_MW 30-FM_AM 31-FM_CM2 |  | int
INPUT_REGISTER | Read | 1705 |  | i2c | Slot1 Error State |  |  | 0-No_Error 1-No_Response 2-Wrong_Module 3-Unsupported_Module 4-Internal_Sw_Error 5-Communication_Failed 6-Internal_Module_Error 7-Module_Not_Supported_Current_Variant 8-Module_Not_Suppported_In_Slot 9-Module_Count_Too_High 10-Module_Not_Supported_With_Connected_Boiler_Type |  | int
INPUT_REGISTER | Read | 1706 |  | i2c | Slot2 Module Detected |  |  | 0-Unknown 1-None 22-FM_CM 25-FM_SI 28-FM_MM 29-FM_MW 30-FM_AM 31-FM_CM2 |  | int
INPUT_REGISTER | Read | 1707 |  | i2c | Slot2 Error State |  |  | 0-No_Error 1-No_Response 2-Wrong_Module 3-Unsupported_Module 4-Internal_Sw_Error 5-Communication_Failed 6-Internal_Module_Error 7-Module_Not_Supported_Current_Variant 8-Module_Not_Suppported_In_Slot 9-Module_Count_Too_High 10-Module_Not_Supported_With_Connected_Boiler_Type |  | int
INPUT_REGISTER | Read | 1708 |  | i2c | Slot3 Module Detected |  |  | 0-Unknown 1-None 22-FM_CM 25-FM_SI 28-FM_MM 29-FM_MW 30-FM_AM 31-FM_CM2 |  | int
INPUT_REGISTER | Read | 1709 |  | i2c | Slot3 Error State |  |  | 0-No_Error 1-No_Response 2-Wrong_Module 3-Unsupported_Module 4-Internal_Sw_Error 5-Communication_Failed 6-Internal_Module_Error 7-Module_Not_Supported_Current_Variant 8-Module_Not_Suppported_In_Slot 9-Module_Count_Too_High 10-Module_Not_Supported_With_Connected_Boiler_Type |  | int
INPUT_REGISTER | Read | 1710 |  | i2c | Slot4 Module Detected |  |  | 0-Unknown 1-None 22-FM_CM 25-FM_SI 28-FM_MM 29-FM_MW 30-FM_AM 31-FM_CM2 |  | int
INPUT_REGISTER | Read | 1711 |  | i2c | Slot4 Error State |  |  | 0-No_Error 1-No_Response 2-Wrong_Module 3-Unsupported_Module 4-Internal_Sw_Error 5-Communication_Failed 6-Internal_Module_Error 7-Module_Not_Supported_Current_Variant 8-Module_Not_Suppported_In_Slot 9-Module_Count_Too_High 10-Module_Not_Supported_With_Connected_Boiler_Type |  | int
INPUT_REGISTER | Read | 1712 |  | i2c | Slot A Module Detected |  |  | 0-Unknown 1-None 26-ZM5313 27-ZM5311 |  | int
INPUT_REGISTER | Read | 1713 |  | i2c | Slot A Error State |  |  | 0-No_Error 1-No_Response 2-Wrong_Module 3-Unsupported_Module 4-Internal_Sw_Error 5-Communication_Failed 6-Internal_Module_Error 7-Module_Not_Supported_Current_Variant 8-Module_Not_Suppported_In_Slot 9-Module_Count_Too_High 10-Module_Not_Supported_With_Connected_Boiler_Type |  | int
INPUT_REGISTER | Read | 1714 |  | i2c | irBitblock |  |  |  |  | int
| Read |  | 0 | i2c | Component Error |  |  |  |  | bit
INPUT_REGISTER | Read | 1725 |  | fm-si | irBitblock |  |  |  |  | int
| Read |  | 0 | fm-si | Input 1 Error |  |  |  |  | bit
| Read |  | 1 | fm-si | Input 2 Error |  |  |  |  | bit
| Read |  | 2 | fm-si | Input 3 Error |  |  |  |  | bit
| Read |  | 3 | fm-si | Input 4 Error |  |  |  |  | bit
| Read |  | 4 | fm-si | Input 5 Error |  |  |  |  | bit
INPUT_REGISTER | Read | 1732 |  | Sdc | Demand Mode (Low Priority) | 0 | 2 | 0-Off 1-Take_Heat 2-Give_Heat |  | int
INPUT_REGISTER | Read | 1733 |  | Sdc | Demand Flow Temp (Low Priority) |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1734 |  | Sdc | Demand Mode (High Priority) | 0 | 2 | 0-Off 1-Take_Heat 2-Give_Heat |  | int
INPUT_REGISTER | Read | 1735 |  | Sdc | Demand Flow Temp (High Priority) |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1739 |  | Heat Pump | System return temperature for HP heating buffer |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1740 |  | Heat Pump | Buffer mid temperature for HP heating buffer |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1741 |  | Heat Pump | Buffer top temperature for HP heating buffer |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1742 |  | Heat Pump | Buffer bottom temperature for HP heating buffer |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1743 |  | Heat Pump | Return temperature FWR |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1744 |  | Heat Pump | Flow temperature FWV |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1745 |  | Heat Pump | Flow temperature HP |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1746 |  | Heat Pump | Return temperature HP |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1747 |  | Heat Pump | HMI State of HP Component | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 1748 |  | Heat Pump | HP current heat output |  |  |  | kW | signed int | x10
INPUT_REGISTER | Read | 1749 |  | Heat Pump | HP current electrical power consumption | 0 | 10000 |  | kW | int | x10
INPUT_REGISTER | Read | 1750 |  | Heat Pump | HP Smart grid mode | 0 | 3 | 0-normal_charging_grid 1-low_charging_grid 2-high_charging_grid 3-free_charging_grid |  | int
INPUT_REGISTER | Read | 1751 |  | Heat Pump | Heat demand temperature set point |  |  |  | °C | int
INPUT_REGISTER | Read | 1752 |  | Heat Pump | heatPumpStatusIrBitblock | 0 |  |  |  | int
INPUT_REGISTER | Read | 1753 |  | Heat Pump | Ambient Temperature HP |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1754 |  | Heat Pump | HP silent mode | 0 | 3 | 0-standard_mode 1-silent_mode 2-super_silent_mode 3-night_mode |  | int
INPUT_REGISTER | Read | 1755 |  | Heat Pump | Heat Pump Heat Request Temperature |  |  |  | °C | int
INPUT_REGISTER | Read | 1756 |  | Heat Pump | heatPumpIrBitblock |  |  |  |  | int
INPUT_REGISTER | Read | 1765 |  | System | Open Notifications Count |  |  |  |  | int
INPUT_REGISTER | Read | 1766 |  | System | Error Key 5 |  |  |  |  | long
INPUT_REGISTER | Read | 1768 |  | System | Error Key 6 |  |  |  |  | long
INPUT_REGISTER | Read | 1770 |  | System | Error Key 7 |  |  |  |  | long
INPUT_REGISTER | Read | 1772 |  | System | Error Key 8 |  |  |  |  | long
INPUT_REGISTER | Read | 1774 |  | System | Error Key 9 |  |  |  |  | long
INPUT_REGISTER | Read | 1776 |  | System | Error Key 10 |  |  |  |  | long
INPUT_REGISTER | Read | 1778 |  | Chp / EC Power | Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1779 |  | Chp / EC Power | Return Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1780 |  | Chp | Flue Gas Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1781 |  | Chp | Motor Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1782 |  | Chp / EC Power | Current Generator Power |  |  |  | kW | int
INPUT_REGISTER | Read | 1783 |  | Chp | Current Power Setpoint |  |  |  | kW | int
INPUT_REGISTER | Read | 1784 |  | Chp / EC Power | Operation Hours |  |  |  | h | long
INPUT_REGISTER | Read | 1786 |  | Chp / EC Power | Number of starts |  |  |  |  | long
INPUT_REGISTER | Read | 1788 |  | Chp / EC Power | Hours to Maintenance |  |  |  | h | int
INPUT_REGISTER | Read | 1790 |  | Chp | Output Power Setpoint |  |  |  | kW | int
INPUT_REGISTER | Read | 1791 |  | Chp | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 1796 |  | Chp | irBitblock |  |  |  |  | int
| Read |  | 0 | Chp | Warning |  |  |  |  | bit
| Read |  | 1 | Chp / EC Power | Malfunction |  |  |  |  | bit
| Read |  | 2 | Chp / EC Power | Controlled Shutdown |  |  |  |  | bit
| Read |  | 3 | Chp / EC Power | Generator On |  |  |  |  | bit
| Read |  | 4 | Chp | Automatic On |  |  |  |  | bit
| Read |  | 5 | Chp / EC Power | Automatic Ready |  |  |  |  | bit
| Read |  | 11 | Chp / EC Power | Output On Request |  |  |  |  | bit
INPUT_REGISTER | Read | 1804 |  | Water Treatment Module | Program Step |  |  | 20-140: Desalination not active 10000-10810: One time desalination 20000-20810: Automatic desalination 30000-30260: Stationary operation |  | int
INPUT_REGISTER | Read | 1805 |  | Water Treatment Module | Temperature Desalinization |  |  |  | °C | int | x10
INPUT_REGISTER | Read | 1806 |  | Water Treatment Module | Volume Flow |  |  |  | L/min | int | x10
INPUT_REGISTER | Read | 1807 |  | Water Treatment Module | Conductivity system |  |  |  | uS/cm | int | x10
INPUT_REGISTER | Read | 1808 |  | Water Treatment Module | Conductivity cartridge |  |  |  | uS/cm | int | x10
INPUT_REGISTER | Read | 1809 |  | Water Treatment Module | Cartridge Capacity |  |  |  | % | int
INPUT_REGISTER | Read | 1813 |  | Solar Data | Collector temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1814 |  | Solar Data | Temperature cylinder bottom |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1815 |  | Solar Data | Solar pump modulation setpoint |  |  |  | % | int
INPUT_REGISTER | Read | 1816 |  | Solar | Solar pump status | 0 | 19 | 1-TestMod 2-BlckProt 3-No heat 4-Ht avail 5-SolOff 6-MaxCyl 7-MaxColl 8-MinColl 9-FrostP 10-VacFct 11-SwChck 12-MixPrio 13-Switch 14-Priority 15-ThermD 16-MixCal 17-MixOpn 18-MixCl 19-MixOff |  | int
INPUT_REGISTER | Read | 1817 |  | Solar Data | Heat exchanger temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1818 |  | Solar Data | Heat exchanger pump modulation setpoint |  |  |  | % | int
INPUT_REGISTER | Read | 1819 |  | Solar | Heat exchanger pump status | 0 | 19 | 1-TestMod 2-BlckProt 3-No heat 4-Ht avail 5-SolOff 6-MaxCyl 7-MaxColl 8-MinColl 9-FrostP 10-VacFct 11-SwChck 12-MixPrio 13-Switch 14-Priority 15-ThermD 16-MixCal 17-MixOpn 18-MixCl 19-MixOff |  | int
INPUT_REGISTER | Read | 1820 |  | Solar Data | Temperature cylinder 3 top |  |  |  | °C | int | x10
INPUT_REGISTER | Read | 1821 |  | Solar Data | Reload pump modulation setpoint |  |  |  | % | int
INPUT_REGISTER | Read | 1822 |  | Solar | Reload pump status | 0 | 19 | 1-TestMod 2-BlckProt 3-No heat 4-Ht avail 5-SolOff 6-MaxCyl 7-MaxColl 8-MinColl 9-FrostP 10-VacFct 11-SwChck 12-MixPrio 13-Switch 14-Priority 15-ThermD 16-MixCal 17-MixOpn 18-MixCl 19-MixOff |  | int
INPUT_REGISTER | Read | 1823 |  | Solar | Pump therm. disinfect. status | 0 | 19 | 1-TestMod 2-BlckProt 3-No heat 4-Ht avail 5-SolOff 6-MaxCyl 7-MaxColl 8-MinColl 9-FrostP 10-VacFct 11-SwChck 12-MixPrio 13-Switch 14-Priority 15-ThermD 16-MixCal 17-MixOpn 18-MixCl 19-MixOff |  | int
INPUT_REGISTER | Read | 1824 |  | Solar Yield | Flow temperature heat meter |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1825 |  | Solar Yield | Return temperature heat meter |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1826 |  | Solar Yield | Heat count pulse counter | 0 | 15 |  |  | int
INPUT_REGISTER | Read | 1827 |  | Solar Yield | Solar yield per month |  |  |  | kWh | long | x10
INPUT_REGISTER | Read | 1829 |  | Solar Yield | Solar yield per year |  |  |  | kWh | long | x10
INPUT_REGISTER | Read | 1831 |  | Solar Yield | Last hour solar yield |  |  |  | kWh | long | x10
INPUT_REGISTER | Read | 1833 |  | Solar Yield | Solar yield per day |  |  |  | kWh | long | x10
INPUT_REGISTER | Read | 1835 |  | Solar Yield | Solar yield since installation |  |  |  | kWh | long | x10
INPUT_REGISTER | Read | 1837 |  | Solar | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 1838 |  | Solar Data | Hydraulic configuration |  |  |  |  | int
| Read |  | 0 | Solar | Option 1 active |  |  |  |  | bit
| Read |  | 1 | Solar | Option A active |  |  |  |  | bit
| Read |  | 2 | Solar | Option B active |  |  |  |  | bit
| Read |  | 3 | Solar | Option C active |  |  |  |  | bit
| Read |  | 4 | Solar | Option D active |  |  |  |  | bit
| Read |  | 5 | Solar | Option E active |  |  |  |  | bit
| Read |  | 6 | Solar | Option F active |  |  |  |  | bit
| Read |  | 7 | Solar | Option G active |  |  |  |  | bit
| Read |  | 8 | Solar | Option H active |  |  |  |  | bit
| Read |  | 9 | Solar | Option I active |  |  |  |  | bit
| Read |  | 10 | Solar | Option J active |  |  |  |  | bit
| Read |  | 11 | Solar | Option K active |  |  |  |  | bit
| Read |  | 12 | Solar | Option L active |  |  |  |  | bit
| Read |  | 13 | Solar | Option M active |  |  |  |  | bit
| Read |  | 14 | Solar | Option N active |  |  |  |  | bit
| Read |  | 15 | Solar | Option P active |  |  |  |  | bit
INPUT_REGISTER | Read | 1839 |  | Solar Data | irBitblock |  |  |  |  | int
| Read |  | 0 | Solar | Is Active |  |  |  |  | bit
INPUT_REGISTER |  | 1900 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 1901 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 1902 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 1903 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 1904 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 1905 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 1906 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 1907 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 1908 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 1909 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 1910 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 1911 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 1912 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 1913 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER | Read | 1922 |  | Energy Monitoring | Heat Output |  |  |  | kW | signed int | x10
INPUT_REGISTER | Read | 1923 |  | Energy Monitoring | Gas Consumption (LCV) |  |  |  | kW | signed int | x10
INPUT_REGISTER | Read | 1925 |  | Energy Monitoring | Electrical Power |  |  |  | W | int
INPUT_REGISTER | Read | 1930 |  | Fresh Water Characteristics 1 | DHW Out Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1931 |  | Fresh Water Characteristics 1 | DHW Volume Flow |  |  |  | L/min | signed int | x10
INPUT_REGISTER | Read | 1932 |  | Fresh Water Characteristics 1 | Prim In Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1933 |  | Fresh Water Characteristics 1 | DHW In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1934 |  | Fresh Water Characteristics 1 | Primary Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 1935 |  | Fresh Water Characteristics 1 | Request DHW Out Temperature |  |  |  | °C | int
INPUT_REGISTER | Read | 1936 |  | Fresh Water Characteristics 1 | Status Request DHW Out Temperature | 0 | 9 | 0-Off 1-DHWRed 2-DHW 3-Sol_red 4-Once_on 5-Therm_d 6-DlyHtUp 7-Preheat_start 8-Preheat_normal 9-No_eq |  | int
INPUT_REGISTER | Read | 1937 |  | Fresh Water Characteristics 2 | Circulation Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 1938 |  | Fresh Water Characteristics 2 | Status Circulation Pump | 0 | 8 | 0-Undefined 1-Test 2-BlckProt 3-No_req 4-AutoOff 5-AutoOn 6-Therm_d 7-Sys_Off 8-DlyHtUp |  | int
INPUT_REGISTER | Read | 1939 |  | Fresh Water Characteristics 2 | Return Valve Modulation Request |  |  |  | % | int
INPUT_REGISTER | Read | 1940 |  | Fresh Water Characteristics 2 | Valve State | 0 | 5 | 0-Undefined 1-TestMod 2-BlckProt 3-Mix_cl 4-Mix_opn 5-Sys_Off |  | int
INPUT_REGISTER | Read | 1941 |  | Fresh Water Characteristics 2 | Return Valve Buffer Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1942 |  | Fresh Water Characteristics 2 | Disinfection Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 1943 |  | Fresh Water Characteristics 2 | Pump State | 0 | 5 | 0-Undefined 1-TestMod 2-BlckPro 3-No_eq 4-Ht_req 5-Sys_Off |  | int
INPUT_REGISTER | Read | 1944 |  | Fresh Water Characteristics 1 | DHW Valve Power |  |  |  | % | int
INPUT_REGISTER | Read | 1945 |  | Fresh Water Characteristics 2 | Total Flow |  |  |  | L/min | int | x10
INPUT_REGISTER | Read | 1946 |  | Fresh Water 2 | Module 2 DHW Out Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1947 |  | Fresh Water 2 | Module 2 DHW Volume Flow |  |  |  | L/min | signed int | x10
INPUT_REGISTER | Read | 1948 |  | Fresh Water 2 | Module 2 Prim In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1949 |  | Fresh Water 2 | Module 2 DHW In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1950 |  | Fresh Water 2 | Module 2 DHW Valve Power |  |  |  | % | int
INPUT_REGISTER | Read | 1951 |  | Fresh Water 2 | Module 2 Prim Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 1952 |  | Fresh Water 2 | Module 2 Status Prim Pump |  |  |  |  | int
INPUT_REGISTER | Read | 1953 |  | Fresh Water 3 | Module 3 DHW Out Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1954 |  | Fresh Water 3 | Module 3 DHW Volume Flow |  |  |  | L/min | signed int | x10
INPUT_REGISTER | Read | 1955 |  | Fresh Water 3 | Module 3 Prim In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1956 |  | Fresh Water 3 | Module 3 DHW In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1957 |  | Fresh Water 3 | Module 3 DHW Valve Power |  |  |  | % | int
INPUT_REGISTER | Read | 1958 |  | Fresh Water 3 | Module 3 Prim Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 1959 |  | Fresh Water 3 | Module 3 Status Prim Pump |  |  |  |  | int
INPUT_REGISTER | Read | 1960 |  | Fresh Water 4 | Module 4 DHW Out Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1961 |  | Fresh Water 4 | Module 4 DHW Volume Flow |  |  |  | L/min | signed int | x10
INPUT_REGISTER | Read | 1962 |  | Fresh Water 4 | Module 4 Prim In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1963 |  | Fresh Water 4 | Module 4 DHW In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 1964 |  | Fresh Water 4 | Module 4 DHW ValvePower |  |  |  | % | int
INPUT_REGISTER | Read | 1965 |  | Fresh Water 4 | Module 4 Prim Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 1966 |  | Fresh Water 4 | Module 4 Status Primary Pump |  |  |  |  | int
INPUT_REGISTER | Read | 1967 |  | Fresh Water | Fresh Water Hmi State |  |  |  |  | int
INPUT_REGISTER | Read | 1968 |  | Fresh Water Characteristics 3 | Fresh Water Configurations |  |  |  |  | int
| Read |  | 0 | Fresh Water | Option 2 active |  |  |  |  | bit
| Read |  | 1 | Fresh Water | Option A active |  |  |  |  | bit
| Read |  | 2 | Fresh Water | Option B active |  |  |  |  | bit
| Read |  | 3 | Fresh Water | Option C active |  |  |  |  | bit
| Read |  | 4 | Fresh Water | Option D active |  |  |  |  | bit
| Read |  | 5 | Fresh Water | Option E active |  |  |  |  | bit
| Read |  | 6 | Fresh Water | Option E active cascade module 2 active |  |  |  |  | bit
| Read |  | 7 | Fresh Water | Option E active cascade module 3 active |  |  |  |  | bit
| Read |  | 8 | Fresh Water | Option E active cascade module 4 active |  |  |  |  | bit
| Read |  | 9 | Fresh Water | Is Active |  |  |  |  | bit
INPUT_REGISTER | Read | 1976 |  | System | Error Key 1 |  |  |  |  | long
INPUT_REGISTER | Read | 1978 |  | System | Error Key 2 |  |  |  |  | long
INPUT_REGISTER | Read | 1980 |  | System | Error Key 3 |  |  |  |  | long
INPUT_REGISTER | Read | 1982 |  | System | Error Key 4 |  |  |  |  | long
INPUT_REGISTER | Read | 1984 |  | System | Error 1 Extra Info (MSB) |  |  |  |  | long
INPUT_REGISTER | Read | 1986 |  | System | Error 1 Extra Info (LSB) |  |  |  |  | long
INPUT_REGISTER | Read | 1988 |  | System | Error 2 Extra Info (MSB) |  |  |  |  | long
INPUT_REGISTER | Read | 1990 |  | System | Error 2 Extra Info (LSB) |  |  |  |  | long
INPUT_REGISTER | Read | 1992 |  | System | Error 3 Extra Info (MSB) |  |  |  |  | long
INPUT_REGISTER | Read | 1994 |  | System | Error 3 Extra Info (LSB) |  |  |  |  | long
INPUT_REGISTER | Read | 1996 |  | System | Error 4 Extra Info (MSB) |  |  |  |  | long
INPUT_REGISTER | Read | 1998 |  | System | Error 4 Extra Info (LSB) |  |  |  |  | long

## Slave04
Register Type | Permissions | Address | Bitblock Bit | Component | Name | Min | Max | Range | Unit | DataType | Float to Int Factor
HOLDING_REGISTER | Write | 2007 |  | DomesticHotWater Zm/Ems | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 2008 |  | DomesticHotWater Zm/Ems | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 2009 |  | DomesticHotWater Zm/Ems | Thermal Disinfection Setpoint | 65 | 75 |  | °C | int | x10
HOLDING_REGISTER | Write | 2010 |  | DomesticHotWater Zm | Setpoint Auto Day | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 2011 |  | DomesticHotWater Zm | Setpoint Auto Night | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 2012 |  | DomesticHotWater Zm | Setpoint Manual Day | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 2013 |  | DomesticHotWater Zm | Setpoint Manual Night | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 2014 |  | DomesticHotWater Zm | Setpoint Holiday | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 2015 |  | DomesticHotWater Zm/Ems | Circulation Pump Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 2016 |  | DomesticHotWater Zm/Ems | Circulation Pump Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 2017 |  | DomesticHotWater Zm/Ems | Disinfection Frequency | 0 | 7 | 0-Daily 1-Monday 2-Tuesday 3-Wednesday 4-Thursday 5-Friday 6-Saturday 7-Sunday |  | int
HOLDING_REGISTER | Write | 2018 |  | DomesticHotWater Zm/Ems | Disinfection Start Hour | 0 | 23 |  | h | int
HOLDING_REGISTER | Write | 2021 |  | DomesticHotWater Fm | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 2022 |  | DomesticHotWater Fm | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 2023 |  | DomesticHotWater Fm | Thermal Disinfection Setpoint | 65 | 75 |  | °C | int | x10
HOLDING_REGISTER | Write | 2024 |  | DomesticHotWater Fm | Setpoint Auto Day | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 2025 |  | DomesticHotWater Fm | Setpoint Auto Night | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 2026 |  | DomesticHotWater Fm | Setpoint Manual Day | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 2027 |  | DomesticHotWater Fm | Setpoint Manual Night | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 2028 |  | DomesticHotWater Fm | Setpoint Holiday | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 2029 |  | DomesticHotWater Fm | Circulation Pump Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 2030 |  | DomesticHotWater Fm | Circulation Pump Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 2031 |  | DomesticHotWater Fm | Disinfection Frequency | 0 | 7 | 0-Daily 1-Monday 2-Tuesday 3-Wednesday 4-Thursday 5-Friday 6-Saturday 7-Sunday |  | int
HOLDING_REGISTER | Write | 2032 |  | DomesticHotWater Fm | Disinfection Start Hour | 0 | 23 |  | h | int
HOLDING_REGISTER | Read | 2039 |  | Boiler | Control Type | 0 | 4 | 0-None 1-Safe 2-Ems 3-7Pole 4-Substation |  | int
HOLDING_REGISTER | Write | 2043 |  | AlternativeHeatSource | Operation Mode Request Auto Day | 20 | 99 |  | °C | int
HOLDING_REGISTER | Write | 2044 |  | AlternativeHeatSource | Operation Mode Request Auto Night | 20 | 99 |  | °C | int
HOLDING_REGISTER | Write | 2045 |  | AlternativeHeatSource | Operation Mode Request Manual Day | 20 | 99 |  | °C | int
HOLDING_REGISTER | Write | 2046 |  | AlternativeHeatSource | Operation Mode Request Manual Night | 20 | 99 |  | °C | int
HOLDING_REGISTER | Write | 2047 |  | AlternativeHeatSource | Operation Mode Request Holiday | 20 | 99 |  | °C | int
HOLDING_REGISTER | Write | 2048 |  | AlternativeHeatSource | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 2049 |  | AlternativeHeatSource | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 2050 |  | AlternativeHeatSource | Return Control Setpoint User | 10 | 70 |  | °C | int
HOLDING_REGISTER | Write | 2057 |  | HydraulicCircuit Zm | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 2058 |  | HydraulicCircuit Zm | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 2059 |  | HydraulicCircuit Zm | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2060 |  | HydraulicCircuit Zm | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2061 |  | HydraulicCircuit Zm | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2062 |  | HydraulicCircuit Zm | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2063 |  | HydraulicCircuit Zm | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2064 |  | HydraulicCircuit Zm | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 2070 |  | HydraulicCircuit 1 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 2071 |  | HydraulicCircuit 1 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 2072 |  | HydraulicCircuit 1 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2073 |  | HydraulicCircuit 1 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2074 |  | HydraulicCircuit 1 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2075 |  | HydraulicCircuit 1 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2076 |  | HydraulicCircuit 1 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2077 |  | HydraulicCircuit 1 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 2083 |  | HydraulicCircuit 2 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 2084 |  | HydraulicCircuit 2 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 2085 |  | HydraulicCircuit 2 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2086 |  | HydraulicCircuit 2 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2087 |  | HydraulicCircuit 2 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2088 |  | HydraulicCircuit 2 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2089 |  | HydraulicCircuit 2 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2090 |  | HydraulicCircuit 2 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 2096 |  | HydraulicCircuit 3 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 2097 |  | HydraulicCircuit 3 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 2098 |  | HydraulicCircuit 3 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2099 |  | HydraulicCircuit 3 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2100 |  | HydraulicCircuit 3 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2101 |  | HydraulicCircuit 3 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2102 |  | HydraulicCircuit 3 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2103 |  | HydraulicCircuit 3 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 2109 |  | HydraulicCircuit 4 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 2110 |  | HydraulicCircuit 4 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 2111 |  | HydraulicCircuit 4 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2112 |  | HydraulicCircuit 4 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2113 |  | HydraulicCircuit 4 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2114 |  | HydraulicCircuit 4 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2115 |  | HydraulicCircuit 4 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2116 |  | HydraulicCircuit 4 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 2122 |  | HydraulicCircuit 5 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 2123 |  | HydraulicCircuit 5 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 2124 |  | HydraulicCircuit 5 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2125 |  | HydraulicCircuit 5 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2126 |  | HydraulicCircuit 5 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2127 |  | HydraulicCircuit 5 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2128 |  | HydraulicCircuit 5 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2129 |  | HydraulicCircuit 5 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 2135 |  | HydraulicCircuit 6 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 2136 |  | HydraulicCircuit 6 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 2137 |  | HydraulicCircuit 6 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2138 |  | HydraulicCircuit 6 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2139 |  | HydraulicCircuit 6 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2140 |  | HydraulicCircuit 6 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2141 |  | HydraulicCircuit 6 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2142 |  | HydraulicCircuit 6 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 2148 |  | HydraulicCircuit 7 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 2149 |  | HydraulicCircuit 7 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 2150 |  | HydraulicCircuit 7 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2151 |  | HydraulicCircuit 7 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2152 |  | HydraulicCircuit 7 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2153 |  | HydraulicCircuit 7 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2154 |  | HydraulicCircuit 7 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2155 |  | HydraulicCircuit 7 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 2161 |  | HydraulicCircuit 8 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 2162 |  | HydraulicCircuit 8 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 2163 |  | HydraulicCircuit 8 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2164 |  | HydraulicCircuit 8 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2165 |  | HydraulicCircuit 8 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2166 |  | HydraulicCircuit 8 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2167 |  | HydraulicCircuit 8 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2168 |  | HydraulicCircuit 8 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 2201 |  | Heat Pump | Heat demand source | 0 | 2 | 0-Scheduler 1-System 2-Max_system_scheduler |  | int
HOLDING_REGISTER | Read | 2421 |  | Fresh Water Characteristics 3 | DHU Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 2422 |  | Fresh Water Characteristics 3 | Extra Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 2423 |  | Fresh Water Characteristics 3 | Maximum DHW Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 2424 |  | Fresh Water Characteristics 3 | On High Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 2425 |  | Fresh Water Characteristics 3 | On Low Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 2426 |  | Fresh Water Characteristics 3 | Fresh Water Type | 0 | 3 | 0-15/20l/min 1-27l/min 2-40l/min 3-60l/min |  | int
HOLDING_REGISTER | Read | 2427 |  | Fresh Water Characteristics 3 | Enable Alarm Output | 0 | 2 | 0-No 1-Yes 2-Inverted |  | int
HOLDING_REGISTER | Read | 2428 |  | Fresh Water Characteristics 3 | Buffer Cylinder Temperature Offset |  |  |  | K | int
HOLDING_REGISTER | Read | 2429 |  | Fresh Water Characteristics 3 | hrBitblock |  |  |  |  | int
| Read |  | 0 | Fresh Water | Buffer Cylinder Temperature Optimization Enabled |  |  |  |  | bit
| Read |  | 1 | Fresh Water | Impulse Enabled |  |  |  |  | bit
| Read |  | 2 | Fresh Water | Time Program Enabled |  |  |  |  | bit
HOLDING_REGISTER | Read | 2430 |  | Fresh Water Characteristics 3 | Minimum Buffer Cylinder Temperature Offset |  |  |  | K | int
HOLDING_REGISTER | Read | 2431 |  | Fresh Water Characteristics 2 | Circulation Pump Runs per Hour | 0 | 7 | 0-Undefined 1-1x3_minutes/h 2-2x3_minutes/h 3-3x3_minutes/h 4-4x3_minutes/h 5-5x3_minutes/h 6-6x3_minutes/h 7-Permanent |  | int
HOLDING_REGISTER | Read | 2432 |  | Fresh Water Characteristics 2 | Swich Hysteresis |  |  |  | K | int
HOLDING_REGISTER | Read | 2433 |  | Fresh Water Characteristics 2 | Thermal Disinfection Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 2434 |  | Fresh Water Characteristics 2 | Pre Heat Maximum Temperature |  |  |  | °C | int
INPUT_REGISTER | Read | 2000 |  | System | Own Outdoor temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2001 |  | System | Damped Own outdoor temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2004 |  | System | Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2008 |  | System | Active Functions 1 |  |  |  |  | int
INPUT_REGISTER | Read | 2009 |  | System | Active Functions 2 |  |  |  |  | int
INPUT_REGISTER | Read | 2015 |  | DomesticHotWater Zm | Charge Pump Running | 0 | 4 | 0-Stopping 1-Starting 2-Running 3-Off 4-Error |  | int
INPUT_REGISTER | Read | 2016 |  | DomesticHotWater Zm | Circulation Pump Running | 0 | 4 | 0-Stopping 1-Starting 2-Running 3-Off 4-Error |  | int
INPUT_REGISTER | Read | 2017 |  | DomesticHotWater Zm | Hydraulic State | 0 | 7 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Cold_load 6-Post_purge 7-Condense_protection |  | int
INPUT_REGISTER | Read | 2018 |  | DomesticHotWater Zm/Ems | Thermal Disinfection Status | 0 | 3 | 0-Off 1-On 2-Success 3-Error |  | int
INPUT_REGISTER | Read | 2019 |  | DomesticHotWater Zm/Ems | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 2020 |  | DomesticHotWater Zm/Ems | Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2021 |  | DomesticHotWater Zm/Ems | Current Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2031 |  | DomesticHotWater Fm | Charge Pump Running | 0 | 4 | 0-Stopping 1-Starting 2-Running 3-Off 4-Error |  | int
INPUT_REGISTER | Read | 2032 |  | DomesticHotWater Fm | Circulation Pump Running | 0 | 4 | 0-Stopping 1-Starting 2-Running 3-Off 4-Error |  | int
INPUT_REGISTER | Read | 2033 |  | DomesticHotWater Fm | Hydraulic State | 0 | 7 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Cold_load 6-Post_purge 7-Condense_protection |  | int
INPUT_REGISTER | Read | 2034 |  | DomesticHotWater Fm | Thermal Disinfection Status | 0 | 3 | 0-Off 1-On 2-Success 3-Error |  | int
INPUT_REGISTER | Read | 2035 |  | DomesticHotWater Fm | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 2036 |  | DomesticHotWater Fm | Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2037 |  | DomesticHotWater Fm | Current Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER |  | 2047 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 2048 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 2050 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 2052 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 2053 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 2054 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 2055 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 2056 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 2059 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 2060 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER | Read | 2063 |  | AlternativeHeatSource | Operating hours |  |  |  | h | long
INPUT_REGISTER | Read | 2065 |  | AlternativeHeatSource | Heat Source Starts |  |  |  |  | long
INPUT_REGISTER | Read | 2067 |  | AlternativeHeatSource | Heat Source Hours to Maintenance |  |  |  | h | int
INPUT_REGISTER | Read | 2069 |  | AlternativeHeatSource | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
| Read |  | 0 | AlternativeHeatSource | Is Heat Source On |  |  |  |  | bit
| Read |  | 1 | AlternativeHeatSource | Is Heat Source On Request |  |  |  |  | bit
INPUT_REGISTER | Read | 2087 |  | HydraulicCircuit Zm | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2088 |  | HydraulicCircuit Zm | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2089 |  | HydraulicCircuit Zm | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2090 |  | HydraulicCircuit Zm | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2091 |  | HydraulicCircuit Zm | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 2092 |  | HydraulicCircuit Zm | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 2093 |  | HydraulicCircuit Zm | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 2094 |  | HydraulicCircuit Zm | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 2095 |  | HydraulicCircuit Zm | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 2099 |  | HydraulicCircuit 1 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2100 |  | HydraulicCircuit 1 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2101 |  | HydraulicCircuit 1 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2102 |  | HydraulicCircuit 1 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2103 |  | HydraulicCircuit 1 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 2104 |  | HydraulicCircuit 1 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 2105 |  | HydraulicCircuit 1 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 2106 |  | HydraulicCircuit 1 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 2107 |  | HydraulicCircuit 1 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 2112 |  | HydraulicCircuit 2 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2113 |  | HydraulicCircuit 2 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2114 |  | HydraulicCircuit 2 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2115 |  | HydraulicCircuit 2 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2116 |  | HydraulicCircuit 2 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 2117 |  | HydraulicCircuit 2 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 2118 |  | HydraulicCircuit 2 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 2119 |  | HydraulicCircuit 2 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 2120 |  | HydraulicCircuit 2 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 2125 |  | HydraulicCircuit 3 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2126 |  | HydraulicCircuit 3 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2127 |  | HydraulicCircuit 3 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2128 |  | HydraulicCircuit 3 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2129 |  | HydraulicCircuit 3 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 2130 |  | HydraulicCircuit 3 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 2131 |  | HydraulicCircuit 3 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 2132 |  | HydraulicCircuit 3 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 2133 |  | HydraulicCircuit 3 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 2138 |  | HydraulicCircuit 4 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2139 |  | HydraulicCircuit 4 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2140 |  | HydraulicCircuit 4 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2141 |  | HydraulicCircuit 4 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2142 |  | HydraulicCircuit 4 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 2143 |  | HydraulicCircuit 4 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 2144 |  | HydraulicCircuit 4 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 2145 |  | HydraulicCircuit 4 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 2146 |  | HydraulicCircuit 4 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 2151 |  | HydraulicCircuit 5 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2152 |  | HydraulicCircuit 5 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2153 |  | HydraulicCircuit 5 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2154 |  | HydraulicCircuit 5 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2155 |  | HydraulicCircuit 5 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 2156 |  | HydraulicCircuit 5 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 2157 |  | HydraulicCircuit 5 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 2158 |  | HydraulicCircuit 5 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 2159 |  | HydraulicCircuit 5 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 2164 |  | HydraulicCircuit 6 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2165 |  | HydraulicCircuit 6 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2166 |  | HydraulicCircuit 6 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2167 |  | HydraulicCircuit 6 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2168 |  | HydraulicCircuit 6 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 2169 |  | HydraulicCircuit 6 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 2170 |  | HydraulicCircuit 6 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 2171 |  | HydraulicCircuit 6 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 2172 |  | HydraulicCircuit 6 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 2177 |  | HydraulicCircuit 7 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2178 |  | HydraulicCircuit 7 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2179 |  | HydraulicCircuit 7 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2180 |  | HydraulicCircuit 7 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2181 |  | HydraulicCircuit 7 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 2182 |  | HydraulicCircuit 7 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 2183 |  | HydraulicCircuit 7 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 2184 |  | HydraulicCircuit 7 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 2185 |  | HydraulicCircuit 7 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 2190 |  | HydraulicCircuit 8 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2191 |  | HydraulicCircuit 8 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2192 |  | HydraulicCircuit 8 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2193 |  | HydraulicCircuit 8 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2194 |  | HydraulicCircuit 8 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 2195 |  | HydraulicCircuit 8 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 2196 |  | HydraulicCircuit 8 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 2197 |  | HydraulicCircuit 8 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 2198 |  | HydraulicCircuit 8 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 2203 |  | i2c | Global Error State | 0 | 4 | 0-No_Error 1-i2c_driver_error 2-Wrong_Cycle_Time 3-Missing_Module_Slot 4-Module_Slot_Error |  | int
INPUT_REGISTER | Read | 2204 |  | i2c | Slot1 Module Detected |  |  | 0-Unknown 1-None 22-FM_CM 25-FM_SI 28-FM_MM 29-FM_MW 30-FM_AM 31-FM_CM2 |  | int
INPUT_REGISTER | Read | 2205 |  | i2c | Slot1 Error State |  |  | 0-No_Error 1-No_Response 2-Wrong_Module 3-Unsupported_Module 4-Internal_Sw_Error 5-Communication_Failed 6-Internal_Module_Error 7-Module_Not_Supported_Current_Variant 8-Module_Not_Suppported_In_Slot 9-Module_Count_Too_High 10-Module_Not_Supported_With_Connected_Boiler_Type |  | int
INPUT_REGISTER | Read | 2206 |  | i2c | Slot2 Module Detected |  |  | 0-Unknown 1-None 22-FM_CM 25-FM_SI 28-FM_MM 29-FM_MW 30-FM_AM 31-FM_CM2 |  | int
INPUT_REGISTER | Read | 2207 |  | i2c | Slot2 Error State |  |  | 0-No_Error 1-No_Response 2-Wrong_Module 3-Unsupported_Module 4-Internal_Sw_Error 5-Communication_Failed 6-Internal_Module_Error 7-Module_Not_Supported_Current_Variant 8-Module_Not_Suppported_In_Slot 9-Module_Count_Too_High 10-Module_Not_Supported_With_Connected_Boiler_Type |  | int
INPUT_REGISTER | Read | 2208 |  | i2c | Slot3 Module Detected |  |  | 0-Unknown 1-None 22-FM_CM 25-FM_SI 28-FM_MM 29-FM_MW 30-FM_AM 31-FM_CM2 |  | int
INPUT_REGISTER | Read | 2209 |  | i2c | Slot3 Error State |  |  | 0-No_Error 1-No_Response 2-Wrong_Module 3-Unsupported_Module 4-Internal_Sw_Error 5-Communication_Failed 6-Internal_Module_Error 7-Module_Not_Supported_Current_Variant 8-Module_Not_Suppported_In_Slot 9-Module_Count_Too_High 10-Module_Not_Supported_With_Connected_Boiler_Type |  | int
INPUT_REGISTER | Read | 2210 |  | i2c | Slot4 Module Detected |  |  | 0-Unknown 1-None 22-FM_CM 25-FM_SI 28-FM_MM 29-FM_MW 30-FM_AM 31-FM_CM2 |  | int
INPUT_REGISTER | Read | 2211 |  | i2c | Slot4 Error State |  |  | 0-No_Error 1-No_Response 2-Wrong_Module 3-Unsupported_Module 4-Internal_Sw_Error 5-Communication_Failed 6-Internal_Module_Error 7-Module_Not_Supported_Current_Variant 8-Module_Not_Suppported_In_Slot 9-Module_Count_Too_High 10-Module_Not_Supported_With_Connected_Boiler_Type |  | int
INPUT_REGISTER | Read | 2212 |  | i2c | Slot A Module Detected |  |  | 0-Unknown 1-None 26-ZM5313 27-ZM5311 |  | int
INPUT_REGISTER | Read | 2213 |  | i2c | Slot A Error State |  |  | 0-No_Error 1-No_Response 2-Wrong_Module 3-Unsupported_Module 4-Internal_Sw_Error 5-Communication_Failed 6-Internal_Module_Error 7-Module_Not_Supported_Current_Variant 8-Module_Not_Suppported_In_Slot 9-Module_Count_Too_High 10-Module_Not_Supported_With_Connected_Boiler_Type |  | int
INPUT_REGISTER | Read | 2214 |  | i2c | irBitblock |  |  |  |  | int
| Read |  | 0 | i2c | Component Error |  |  |  |  | bit
INPUT_REGISTER | Read | 2225 |  | fm-si | irBitblock |  |  |  |  | int
| Read |  | 0 | fm-si | Input 1 Error |  |  |  |  | bit
| Read |  | 1 | fm-si | Input 2 Error |  |  |  |  | bit
| Read |  | 2 | fm-si | Input 3 Error |  |  |  |  | bit
| Read |  | 3 | fm-si | Input 4 Error |  |  |  |  | bit
| Read |  | 4 | fm-si | Input 5 Error |  |  |  |  | bit
INPUT_REGISTER | Read | 2232 |  | Sdc | Demand Mode (Low Priority) | 0 | 2 | 0-Off 1-Take_Heat 2-Give_Heat |  | int
INPUT_REGISTER | Read | 2233 |  | Sdc | Demand Flow Temp (Low Priority) |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2234 |  | Sdc | Demand Mode (High Priority) | 0 | 2 | 0-Off 1-Take_Heat 2-Give_Heat |  | int
INPUT_REGISTER | Read | 2235 |  | Sdc | Demand Flow Temp (High Priority) |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2239 |  | Heat Pump | System return temperature for HP heating buffer |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2240 |  | Heat Pump | Buffer mid temperature for HP heating buffer |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2241 |  | Heat Pump | Buffer top temperature for HP heating buffer |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2242 |  | Heat Pump | Buffer bottom temperature for HP heating buffer |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2243 |  | Heat Pump | Return temperature FWR |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2244 |  | Heat Pump | Flow temperature FWV |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2245 |  | Heat Pump | Flow temperature HP |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2246 |  | Heat Pump | Return temperature HP |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2247 |  | Heat Pump | HMI State of HP Component | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 2248 |  | Heat Pump | HP current heat output |  |  |  | kW | signed int | x10
INPUT_REGISTER | Read | 2249 |  | Heat Pump | HP current electrical power consumption | 0 | 10000 |  | kW | int | x10
INPUT_REGISTER | Read | 2250 |  | Heat Pump | HP Smart grid mode | 0 | 3 | 0-normal_charging_grid 1-low_charging_grid 2-high_charging_grid 3-free_charging_grid |  | int
INPUT_REGISTER | Read | 2251 |  | Heat Pump | Heat demand temperature set point |  |  |  | °C | int
INPUT_REGISTER | Read | 2252 |  | Heat Pump | heatPumpStatusIrBitblock | 0 |  |  |  | int
INPUT_REGISTER | Read | 2253 |  | Heat Pump | Ambient Temperature HP |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2254 |  | Heat Pump | HP silent mode | 0 | 3 | 0-standard_mode 1-silent_mode 2-super_silent_mode 3-night_mode |  | int
INPUT_REGISTER | Read | 2255 |  | Heat Pump | Heat Pump Heat Request Temperature |  |  |  | °C | int
INPUT_REGISTER | Read | 2256 |  | Heat Pump | heatPumpIrBitblock |  |  |  |  | int
INPUT_REGISTER | Read | 2265 |  | System | Open Notifications Count |  |  |  |  | int
INPUT_REGISTER | Read | 2266 |  | System | Error Key 5 |  |  |  |  | long
INPUT_REGISTER | Read | 2268 |  | System | Error Key 6 |  |  |  |  | long
INPUT_REGISTER | Read | 2270 |  | System | Error Key 7 |  |  |  |  | long
INPUT_REGISTER | Read | 2272 |  | System | Error Key 8 |  |  |  |  | long
INPUT_REGISTER | Read | 2274 |  | System | Error Key 9 |  |  |  |  | long
INPUT_REGISTER | Read | 2276 |  | System | Error Key 10 |  |  |  |  | long
INPUT_REGISTER | Read | 2278 |  | Chp / EC Power | Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2279 |  | Chp / EC Power | Return Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2280 |  | Chp | Flue Gas Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2281 |  | Chp | Motor Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2282 |  | Chp / EC Power | Current Generator Power |  |  |  | kW | int
INPUT_REGISTER | Read | 2283 |  | Chp | Current Power Setpoint |  |  |  | kW | int
INPUT_REGISTER | Read | 2284 |  | Chp / EC Power | Operation Hours |  |  |  | h | long
INPUT_REGISTER | Read | 2286 |  | Chp / EC Power | Number of starts |  |  |  |  | long
INPUT_REGISTER | Read | 2288 |  | Chp / EC Power | Hours to Maintenance |  |  |  | h | int
INPUT_REGISTER | Read | 2290 |  | Chp | Output Power Setpoint |  |  |  | kW | int
INPUT_REGISTER | Read | 2291 |  | Chp | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 2296 |  | Chp | irBitblock |  |  |  |  | int
| Read |  | 0 | Chp | Warning |  |  |  |  | bit
| Read |  | 1 | Chp / EC Power | Malfunction |  |  |  |  | bit
| Read |  | 2 | Chp / EC Power | Controlled Shutdown |  |  |  |  | bit
| Read |  | 3 | Chp / EC Power | Generator On |  |  |  |  | bit
| Read |  | 4 | Chp | Automatic On |  |  |  |  | bit
| Read |  | 5 | Chp / EC Power | Automatic Ready |  |  |  |  | bit
| Read |  | 11 | Chp / EC Power | Output On Request |  |  |  |  | bit
INPUT_REGISTER | Read | 2304 |  | Water Treatment Module | Program Step |  |  | 20-140: Desalination not active 10000-10810: One time desalination 20000-20810: Automatic desalination 30000-30260: Stationary operation |  | int
INPUT_REGISTER | Read | 2305 |  | Water Treatment Module | Temperature Desalinization |  |  |  | °C | int | x10
INPUT_REGISTER | Read | 2306 |  | Water Treatment Module | Volume Flow |  |  |  | L/min | int | x10
INPUT_REGISTER | Read | 2307 |  | Water Treatment Module | Conductivity system |  |  |  | uS/cm | int | x10
INPUT_REGISTER | Read | 2308 |  | Water Treatment Module | Conductivity cartridge |  |  |  | uS/cm | int | x10
INPUT_REGISTER | Read | 2309 |  | Water Treatment Module | Cartridge Capacity |  |  |  | % | int
INPUT_REGISTER | Read | 2313 |  | Solar Data | Collector temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2314 |  | Solar Data | Temperature cylinder bottom |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2315 |  | Solar Data | Solar pump modulation setpoint |  |  |  | % | int
INPUT_REGISTER | Read | 2316 |  | Solar | Solar pump status | 0 | 19 | 1-TestMod 2-BlckProt 3-No heat 4-Ht avail 5-SolOff 6-MaxCyl 7-MaxColl 8-MinColl 9-FrostP 10-VacFct 11-SwChck 12-MixPrio 13-Switch 14-Priority 15-ThermD 16-MixCal 17-MixOpn 18-MixCl 19-MixOff |  | int
INPUT_REGISTER | Read | 2317 |  | Solar Data | Heat exchanger temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2318 |  | Solar Data | Heat exchanger pump modulation setpoint |  |  |  | % | int
INPUT_REGISTER | Read | 2319 |  | Solar | Heat exchanger pump status | 0 | 19 | 1-TestMod 2-BlckProt 3-No heat 4-Ht avail 5-SolOff 6-MaxCyl 7-MaxColl 8-MinColl 9-FrostP 10-VacFct 11-SwChck 12-MixPrio 13-Switch 14-Priority 15-ThermD 16-MixCal 17-MixOpn 18-MixCl 19-MixOff |  | int
INPUT_REGISTER | Read | 2320 |  | Solar Data | Temperature cylinder 3 top |  |  |  | °C | int | x10
INPUT_REGISTER | Read | 2321 |  | Solar Data | Reload pump modulation setpoint |  |  |  | % | int
INPUT_REGISTER | Read | 2322 |  | Solar | Reload pump status | 0 | 19 | 1-TestMod 2-BlckProt 3-No heat 4-Ht avail 5-SolOff 6-MaxCyl 7-MaxColl 8-MinColl 9-FrostP 10-VacFct 11-SwChck 12-MixPrio 13-Switch 14-Priority 15-ThermD 16-MixCal 17-MixOpn 18-MixCl 19-MixOff |  | int
INPUT_REGISTER | Read | 2323 |  | Solar | Pump therm. disinfect. status | 0 | 19 | 1-TestMod 2-BlckProt 3-No heat 4-Ht avail 5-SolOff 6-MaxCyl 7-MaxColl 8-MinColl 9-FrostP 10-VacFct 11-SwChck 12-MixPrio 13-Switch 14-Priority 15-ThermD 16-MixCal 17-MixOpn 18-MixCl 19-MixOff |  | int
INPUT_REGISTER | Read | 2324 |  | Solar Yield | Flow temperature heat meter |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2325 |  | Solar Yield | Return temperature heat meter |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2326 |  | Solar Yield | Heat count pulse counter | 0 | 15 |  |  | int
INPUT_REGISTER | Read | 2327 |  | Solar Yield | Solar yield per month |  |  |  | kWh | long | x10
INPUT_REGISTER | Read | 2329 |  | Solar Yield | Solar yield per year |  |  |  | kWh | long | x10
INPUT_REGISTER | Read | 2331 |  | Solar Yield | Last hour solar yield |  |  |  | kWh | long | x10
INPUT_REGISTER | Read | 2333 |  | Solar Yield | Solar yield per day |  |  |  | kWh | long | x10
INPUT_REGISTER | Read | 2335 |  | Solar Yield | Solar yield since installation |  |  |  | kWh | long | x10
INPUT_REGISTER | Read | 2337 |  | Solar | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 2338 |  | Solar Data | Hydraulic configuration |  |  |  |  | int
| Read |  | 0 | Solar | Option 1 active |  |  |  |  | bit
| Read |  | 1 | Solar | Option A active |  |  |  |  | bit
| Read |  | 2 | Solar | Option B active |  |  |  |  | bit
| Read |  | 3 | Solar | Option C active |  |  |  |  | bit
| Read |  | 4 | Solar | Option D active |  |  |  |  | bit
| Read |  | 5 | Solar | Option E active |  |  |  |  | bit
| Read |  | 6 | Solar | Option F active |  |  |  |  | bit
| Read |  | 7 | Solar | Option G active |  |  |  |  | bit
| Read |  | 8 | Solar | Option H active |  |  |  |  | bit
| Read |  | 9 | Solar | Option I active |  |  |  |  | bit
| Read |  | 10 | Solar | Option J active |  |  |  |  | bit
| Read |  | 11 | Solar | Option K active |  |  |  |  | bit
| Read |  | 12 | Solar | Option L active |  |  |  |  | bit
| Read |  | 13 | Solar | Option M active |  |  |  |  | bit
| Read |  | 14 | Solar | Option N active |  |  |  |  | bit
| Read |  | 15 | Solar | Option P active |  |  |  |  | bit
INPUT_REGISTER | Read | 2339 |  | Solar Data | irBitblock |  |  |  |  | int
| Read |  | 0 | Solar | Is Active |  |  |  |  | bit
INPUT_REGISTER |  | 2400 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 2401 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 2402 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 2403 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 2404 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 2405 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 2406 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 2407 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 2408 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 2409 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 2410 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 2411 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 2412 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 2413 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER | Read | 2422 |  | Energy Monitoring | Heat Output |  |  |  | kW | signed int | x10
INPUT_REGISTER | Read | 2423 |  | Energy Monitoring | Gas Consumption (LCV) |  |  |  | kW | signed int | x10
INPUT_REGISTER | Read | 2425 |  | Energy Monitoring | Electrical Power |  |  |  | W | int
INPUT_REGISTER | Read | 2430 |  | Fresh Water Characteristics 1 | DHW Out Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2431 |  | Fresh Water Characteristics 1 | DHW Volume Flow |  |  |  | L/min | signed int | x10
INPUT_REGISTER | Read | 2432 |  | Fresh Water Characteristics 1 | Prim In Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2433 |  | Fresh Water Characteristics 1 | DHW In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2434 |  | Fresh Water Characteristics 1 | Primary Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 2435 |  | Fresh Water Characteristics 1 | Request DHW Out Temperature |  |  |  | °C | int
INPUT_REGISTER | Read | 2436 |  | Fresh Water Characteristics 1 | Status Request DHW Out Temperature | 0 | 9 | 0-Off 1-DHWRed 2-DHW 3-Sol_red 4-Once_on 5-Therm_d 6-DlyHtUp 7-Preheat_start 8-Preheat_normal 9-No_eq |  | int
INPUT_REGISTER | Read | 2437 |  | Fresh Water Characteristics 2 | Circulation Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 2438 |  | Fresh Water Characteristics 2 | Status Circulation Pump | 0 | 8 | 0-Undefined 1-Test 2-BlckProt 3-No_req 4-AutoOff 5-AutoOn 6-Therm_d 7-Sys_Off 8-DlyHtUp |  | int
INPUT_REGISTER | Read | 2439 |  | Fresh Water Characteristics 2 | Return Valve Modulation Request |  |  |  | % | int
INPUT_REGISTER | Read | 2440 |  | Fresh Water Characteristics 2 | Valve State | 0 | 5 | 0-Undefined 1-TestMod 2-BlckProt 3-Mix_cl 4-Mix_opn 5-Sys_Off |  | int
INPUT_REGISTER | Read | 2441 |  | Fresh Water Characteristics 2 | Return Valve Buffer Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2442 |  | Fresh Water Characteristics 2 | Disinfection Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 2443 |  | Fresh Water Characteristics 2 | Pump State | 0 | 5 | 0-Undefined 1-TestMod 2-BlckPro 3-No_eq 4-Ht_req 5-Sys_Off |  | int
INPUT_REGISTER | Read | 2444 |  | Fresh Water Characteristics 1 | DHW Valve Power |  |  |  | % | int
INPUT_REGISTER | Read | 2445 |  | Fresh Water Characteristics 2 | Total Flow |  |  |  | L/min | int | x10
INPUT_REGISTER | Read | 2446 |  | Fresh Water 2 | Module 2 DHW Out Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2447 |  | Fresh Water 2 | Module 2 DHW Volume Flow |  |  |  | L/min | signed int | x10
INPUT_REGISTER | Read | 2448 |  | Fresh Water 2 | Module 2 Prim In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2449 |  | Fresh Water 2 | Module 2 DHW In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2450 |  | Fresh Water 2 | Module 2 DHW Valve Power |  |  |  | % | int
INPUT_REGISTER | Read | 2451 |  | Fresh Water 2 | Module 2 Prim Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 2452 |  | Fresh Water 2 | Module 2 Status Prim Pump |  |  |  |  | int
INPUT_REGISTER | Read | 2453 |  | Fresh Water 3 | Module 3 DHW Out Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2454 |  | Fresh Water 3 | Module 3 DHW Volume Flow |  |  |  | L/min | signed int | x10
INPUT_REGISTER | Read | 2455 |  | Fresh Water 3 | Module 3 Prim In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2456 |  | Fresh Water 3 | Module 3 DHW In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2457 |  | Fresh Water 3 | Module 3 DHW Valve Power |  |  |  | % | int
INPUT_REGISTER | Read | 2458 |  | Fresh Water 3 | Module 3 Prim Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 2459 |  | Fresh Water 3 | Module 3 Status Prim Pump |  |  |  |  | int
INPUT_REGISTER | Read | 2460 |  | Fresh Water 4 | Module 4 DHW Out Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2461 |  | Fresh Water 4 | Module 4 DHW Volume Flow |  |  |  | L/min | signed int | x10
INPUT_REGISTER | Read | 2462 |  | Fresh Water 4 | Module 4 Prim In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2463 |  | Fresh Water 4 | Module 4 DHW In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2464 |  | Fresh Water 4 | Module 4 DHW ValvePower |  |  |  | % | int
INPUT_REGISTER | Read | 2465 |  | Fresh Water 4 | Module 4 Prim Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 2466 |  | Fresh Water 4 | Module 4 Status Primary Pump |  |  |  |  | int
INPUT_REGISTER | Read | 2467 |  | Fresh Water | Fresh Water Hmi State |  |  |  |  | int
INPUT_REGISTER | Read | 2468 |  | Fresh Water Characteristics 3 | Fresh Water Configurations |  |  |  |  | int
| Read |  | 0 | Fresh Water | Option 2 active |  |  |  |  | bit
| Read |  | 1 | Fresh Water | Option A active |  |  |  |  | bit
| Read |  | 2 | Fresh Water | Option B active |  |  |  |  | bit
| Read |  | 3 | Fresh Water | Option C active |  |  |  |  | bit
| Read |  | 4 | Fresh Water | Option D active |  |  |  |  | bit
| Read |  | 5 | Fresh Water | Option E active |  |  |  |  | bit
| Read |  | 6 | Fresh Water | Option E active cascade module 2 active |  |  |  |  | bit
| Read |  | 7 | Fresh Water | Option E active cascade module 3 active |  |  |  |  | bit
| Read |  | 8 | Fresh Water | Option E active cascade module 4 active |  |  |  |  | bit
| Read |  | 9 | Fresh Water | Is Active |  |  |  |  | bit
INPUT_REGISTER | Read | 2476 |  | System | Error Key 1 |  |  |  |  | long
INPUT_REGISTER | Read | 2478 |  | System | Error Key 2 |  |  |  |  | long
INPUT_REGISTER | Read | 2480 |  | System | Error Key 3 |  |  |  |  | long
INPUT_REGISTER | Read | 2482 |  | System | Error Key 4 |  |  |  |  | long
INPUT_REGISTER | Read | 2484 |  | System | Error 1 Extra Info (MSB) |  |  |  |  | long
INPUT_REGISTER | Read | 2486 |  | System | Error 1 Extra Info (LSB) |  |  |  |  | long
INPUT_REGISTER | Read | 2488 |  | System | Error 2 Extra Info (MSB) |  |  |  |  | long
INPUT_REGISTER | Read | 2490 |  | System | Error 2 Extra Info (LSB) |  |  |  |  | long
INPUT_REGISTER | Read | 2492 |  | System | Error 3 Extra Info (MSB) |  |  |  |  | long
INPUT_REGISTER | Read | 2494 |  | System | Error 3 Extra Info (LSB) |  |  |  |  | long
INPUT_REGISTER | Read | 2496 |  | System | Error 4 Extra Info (MSB) |  |  |  |  | long
INPUT_REGISTER | Read | 2498 |  | System | Error 4 Extra Info (LSB) |  |  |  |  | long

## Slave05
Register Type | Permissions | Address | Bitblock Bit | Component | Name | Min | Max | Range | Unit | DataType | Float to Int Factor
HOLDING_REGISTER | Write | 2507 |  | DomesticHotWater Zm/Ems | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 2508 |  | DomesticHotWater Zm/Ems | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 2509 |  | DomesticHotWater Zm/Ems | Thermal Disinfection Setpoint | 65 | 75 |  | °C | int | x10
HOLDING_REGISTER | Write | 2510 |  | DomesticHotWater Zm | Setpoint Auto Day | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 2511 |  | DomesticHotWater Zm | Setpoint Auto Night | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 2512 |  | DomesticHotWater Zm | Setpoint Manual Day | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 2513 |  | DomesticHotWater Zm | Setpoint Manual Night | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 2514 |  | DomesticHotWater Zm | Setpoint Holiday | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 2515 |  | DomesticHotWater Zm/Ems | Circulation Pump Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 2516 |  | DomesticHotWater Zm/Ems | Circulation Pump Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 2517 |  | DomesticHotWater Zm/Ems | Disinfection Frequency | 0 | 7 | 0-Daily 1-Monday 2-Tuesday 3-Wednesday 4-Thursday 5-Friday 6-Saturday 7-Sunday |  | int
HOLDING_REGISTER | Write | 2518 |  | DomesticHotWater Zm/Ems | Disinfection Start Hour | 0 | 23 |  | h | int
HOLDING_REGISTER | Write | 2521 |  | DomesticHotWater Fm | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 2522 |  | DomesticHotWater Fm | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 2523 |  | DomesticHotWater Fm | Thermal Disinfection Setpoint | 65 | 75 |  | °C | int | x10
HOLDING_REGISTER | Write | 2524 |  | DomesticHotWater Fm | Setpoint Auto Day | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 2525 |  | DomesticHotWater Fm | Setpoint Auto Night | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 2526 |  | DomesticHotWater Fm | Setpoint Manual Day | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 2527 |  | DomesticHotWater Fm | Setpoint Manual Night | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 2528 |  | DomesticHotWater Fm | Setpoint Holiday | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 2529 |  | DomesticHotWater Fm | Circulation Pump Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 2530 |  | DomesticHotWater Fm | Circulation Pump Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 2531 |  | DomesticHotWater Fm | Disinfection Frequency | 0 | 7 | 0-Daily 1-Monday 2-Tuesday 3-Wednesday 4-Thursday 5-Friday 6-Saturday 7-Sunday |  | int
HOLDING_REGISTER | Write | 2532 |  | DomesticHotWater Fm | Disinfection Start Hour | 0 | 23 |  | h | int
HOLDING_REGISTER | Read | 2539 |  | Boiler | Control Type | 0 | 4 | 0-None 1-Safe 2-Ems 3-7Pole 4-Substation |  | int
HOLDING_REGISTER | Write | 2543 |  | AlternativeHeatSource | Operation Mode Request Auto Day | 20 | 99 |  | °C | int
HOLDING_REGISTER | Write | 2544 |  | AlternativeHeatSource | Operation Mode Request Auto Night | 20 | 99 |  | °C | int
HOLDING_REGISTER | Write | 2545 |  | AlternativeHeatSource | Operation Mode Request Manual Day | 20 | 99 |  | °C | int
HOLDING_REGISTER | Write | 2546 |  | AlternativeHeatSource | Operation Mode Request Manual Night | 20 | 99 |  | °C | int
HOLDING_REGISTER | Write | 2547 |  | AlternativeHeatSource | Operation Mode Request Holiday | 20 | 99 |  | °C | int
HOLDING_REGISTER | Write | 2548 |  | AlternativeHeatSource | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 2549 |  | AlternativeHeatSource | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 2550 |  | AlternativeHeatSource | Return Control Setpoint User | 10 | 70 |  | °C | int
HOLDING_REGISTER | Write | 2557 |  | HydraulicCircuit Zm | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 2558 |  | HydraulicCircuit Zm | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 2559 |  | HydraulicCircuit Zm | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2560 |  | HydraulicCircuit Zm | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2561 |  | HydraulicCircuit Zm | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2562 |  | HydraulicCircuit Zm | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2563 |  | HydraulicCircuit Zm | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2564 |  | HydraulicCircuit Zm | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 2570 |  | HydraulicCircuit 1 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 2571 |  | HydraulicCircuit 1 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 2572 |  | HydraulicCircuit 1 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2573 |  | HydraulicCircuit 1 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2574 |  | HydraulicCircuit 1 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2575 |  | HydraulicCircuit 1 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2576 |  | HydraulicCircuit 1 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2577 |  | HydraulicCircuit 1 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 2583 |  | HydraulicCircuit 2 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 2584 |  | HydraulicCircuit 2 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 2585 |  | HydraulicCircuit 2 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2586 |  | HydraulicCircuit 2 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2587 |  | HydraulicCircuit 2 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2588 |  | HydraulicCircuit 2 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2589 |  | HydraulicCircuit 2 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2590 |  | HydraulicCircuit 2 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 2596 |  | HydraulicCircuit 3 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 2597 |  | HydraulicCircuit 3 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 2598 |  | HydraulicCircuit 3 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2599 |  | HydraulicCircuit 3 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2600 |  | HydraulicCircuit 3 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2601 |  | HydraulicCircuit 3 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2602 |  | HydraulicCircuit 3 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2603 |  | HydraulicCircuit 3 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 2609 |  | HydraulicCircuit 4 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 2610 |  | HydraulicCircuit 4 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 2611 |  | HydraulicCircuit 4 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2612 |  | HydraulicCircuit 4 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2613 |  | HydraulicCircuit 4 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2614 |  | HydraulicCircuit 4 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2615 |  | HydraulicCircuit 4 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2616 |  | HydraulicCircuit 4 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 2622 |  | HydraulicCircuit 5 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 2623 |  | HydraulicCircuit 5 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 2624 |  | HydraulicCircuit 5 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2625 |  | HydraulicCircuit 5 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2626 |  | HydraulicCircuit 5 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2627 |  | HydraulicCircuit 5 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2628 |  | HydraulicCircuit 5 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2629 |  | HydraulicCircuit 5 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 2635 |  | HydraulicCircuit 6 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 2636 |  | HydraulicCircuit 6 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 2637 |  | HydraulicCircuit 6 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2638 |  | HydraulicCircuit 6 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2639 |  | HydraulicCircuit 6 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2640 |  | HydraulicCircuit 6 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2641 |  | HydraulicCircuit 6 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2642 |  | HydraulicCircuit 6 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 2648 |  | HydraulicCircuit 7 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 2649 |  | HydraulicCircuit 7 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 2650 |  | HydraulicCircuit 7 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2651 |  | HydraulicCircuit 7 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2652 |  | HydraulicCircuit 7 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2653 |  | HydraulicCircuit 7 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2654 |  | HydraulicCircuit 7 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2655 |  | HydraulicCircuit 7 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 2661 |  | HydraulicCircuit 8 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 2662 |  | HydraulicCircuit 8 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 2663 |  | HydraulicCircuit 8 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2664 |  | HydraulicCircuit 8 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2665 |  | HydraulicCircuit 8 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2666 |  | HydraulicCircuit 8 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2667 |  | HydraulicCircuit 8 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 2668 |  | HydraulicCircuit 8 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 2701 |  | Heat Pump | Heat demand source | 0 | 2 | 0-Scheduler 1-System 2-Max_system_scheduler |  | int
HOLDING_REGISTER | Read | 2921 |  | Fresh Water Characteristics 3 | DHU Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 2922 |  | Fresh Water Characteristics 3 | Extra Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 2923 |  | Fresh Water Characteristics 3 | Maximum DHW Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 2924 |  | Fresh Water Characteristics 3 | On High Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 2925 |  | Fresh Water Characteristics 3 | On Low Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 2926 |  | Fresh Water Characteristics 3 | Fresh Water Type | 0 | 3 | 0-15/20l/min 1-27l/min 2-40l/min 3-60l/min |  | int
HOLDING_REGISTER | Read | 2927 |  | Fresh Water Characteristics 3 | Enable Alarm Output | 0 | 2 | 0-No 1-Yes 2-Inverted |  | int
HOLDING_REGISTER | Read | 2928 |  | Fresh Water Characteristics 3 | Buffer Cylinder Temperature Offset |  |  |  | K | int
HOLDING_REGISTER | Read | 2929 |  | Fresh Water Characteristics 3 | hrBitblock |  |  |  |  | int
| Read |  | 0 | Fresh Water | Buffer Cylinder Temperature Optimization Enabled |  |  |  |  | bit
| Read |  | 1 | Fresh Water | Impulse Enabled |  |  |  |  | bit
| Read |  | 2 | Fresh Water | Time Program Enabled |  |  |  |  | bit
HOLDING_REGISTER | Read | 2930 |  | Fresh Water Characteristics 3 | Minimum Buffer Cylinder Temperature Offset |  |  |  | K | int
HOLDING_REGISTER | Read | 2931 |  | Fresh Water Characteristics 2 | Circulation Pump Runs per Hour | 0 | 7 | 0-Undefined 1-1x3_minutes/h 2-2x3_minutes/h 3-3x3_minutes/h 4-4x3_minutes/h 5-5x3_minutes/h 6-6x3_minutes/h 7-Permanent |  | int
HOLDING_REGISTER | Read | 2932 |  | Fresh Water Characteristics 2 | Swich Hysteresis |  |  |  | K | int
HOLDING_REGISTER | Read | 2933 |  | Fresh Water Characteristics 2 | Thermal Disinfection Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 2934 |  | Fresh Water Characteristics 2 | Pre Heat Maximum Temperature |  |  |  | °C | int
INPUT_REGISTER | Read | 2500 |  | System | Own Outdoor temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2501 |  | System | Damped Own outdoor temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2504 |  | System | Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2508 |  | System | Active Functions 1 |  |  |  |  | int
INPUT_REGISTER | Read | 2509 |  | System | Active Functions 2 |  |  |  |  | int
INPUT_REGISTER | Read | 2515 |  | DomesticHotWater Zm | Charge Pump Running | 0 | 4 | 0-Stopping 1-Starting 2-Running 3-Off 4-Error |  | int
INPUT_REGISTER | Read | 2516 |  | DomesticHotWater Zm | Circulation Pump Running | 0 | 4 | 0-Stopping 1-Starting 2-Running 3-Off 4-Error |  | int
INPUT_REGISTER | Read | 2517 |  | DomesticHotWater Zm | Hydraulic State | 0 | 7 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Cold_load 6-Post_purge 7-Condense_protection |  | int
INPUT_REGISTER | Read | 2518 |  | DomesticHotWater Zm/Ems | Thermal Disinfection Status | 0 | 3 | 0-Off 1-On 2-Success 3-Error |  | int
INPUT_REGISTER | Read | 2519 |  | DomesticHotWater Zm/Ems | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 2520 |  | DomesticHotWater Zm/Ems | Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2521 |  | DomesticHotWater Zm/Ems | Current Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2531 |  | DomesticHotWater Fm | Charge Pump Running | 0 | 4 | 0-Stopping 1-Starting 2-Running 3-Off 4-Error |  | int
INPUT_REGISTER | Read | 2532 |  | DomesticHotWater Fm | Circulation Pump Running | 0 | 4 | 0-Stopping 1-Starting 2-Running 3-Off 4-Error |  | int
INPUT_REGISTER | Read | 2533 |  | DomesticHotWater Fm | Hydraulic State | 0 | 7 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Cold_load 6-Post_purge 7-Condense_protection |  | int
INPUT_REGISTER | Read | 2534 |  | DomesticHotWater Fm | Thermal Disinfection Status | 0 | 3 | 0-Off 1-On 2-Success 3-Error |  | int
INPUT_REGISTER | Read | 2535 |  | DomesticHotWater Fm | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 2536 |  | DomesticHotWater Fm | Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2537 |  | DomesticHotWater Fm | Current Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER |  | 2547 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 2548 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 2550 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 2552 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 2553 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 2554 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 2555 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 2556 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 2559 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 2560 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER | Read | 2563 |  | AlternativeHeatSource | Operating hours |  |  |  | h | long
INPUT_REGISTER | Read | 2565 |  | AlternativeHeatSource | Heat Source Starts |  |  |  |  | long
INPUT_REGISTER | Read | 2567 |  | AlternativeHeatSource | Heat Source Hours to Maintenance |  |  |  | h | int
INPUT_REGISTER | Read | 2569 |  | AlternativeHeatSource | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
| Read |  | 0 | AlternativeHeatSource | Is Heat Source On |  |  |  |  | bit
| Read |  | 1 | AlternativeHeatSource | Is Heat Source On Request |  |  |  |  | bit
INPUT_REGISTER | Read | 2587 |  | HydraulicCircuit Zm | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2588 |  | HydraulicCircuit Zm | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2589 |  | HydraulicCircuit Zm | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2590 |  | HydraulicCircuit Zm | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2591 |  | HydraulicCircuit Zm | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 2592 |  | HydraulicCircuit Zm | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 2593 |  | HydraulicCircuit Zm | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 2594 |  | HydraulicCircuit Zm | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 2595 |  | HydraulicCircuit Zm | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 2599 |  | HydraulicCircuit 1 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2600 |  | HydraulicCircuit 1 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2601 |  | HydraulicCircuit 1 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2602 |  | HydraulicCircuit 1 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2603 |  | HydraulicCircuit 1 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 2604 |  | HydraulicCircuit 1 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 2605 |  | HydraulicCircuit 1 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 2606 |  | HydraulicCircuit 1 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 2607 |  | HydraulicCircuit 1 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 2612 |  | HydraulicCircuit 2 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2613 |  | HydraulicCircuit 2 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2614 |  | HydraulicCircuit 2 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2615 |  | HydraulicCircuit 2 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2616 |  | HydraulicCircuit 2 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 2617 |  | HydraulicCircuit 2 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 2618 |  | HydraulicCircuit 2 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 2619 |  | HydraulicCircuit 2 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 2620 |  | HydraulicCircuit 2 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 2625 |  | HydraulicCircuit 3 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2626 |  | HydraulicCircuit 3 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2627 |  | HydraulicCircuit 3 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2628 |  | HydraulicCircuit 3 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2629 |  | HydraulicCircuit 3 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 2630 |  | HydraulicCircuit 3 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 2631 |  | HydraulicCircuit 3 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 2632 |  | HydraulicCircuit 3 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 2633 |  | HydraulicCircuit 3 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 2638 |  | HydraulicCircuit 4 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2639 |  | HydraulicCircuit 4 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2640 |  | HydraulicCircuit 4 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2641 |  | HydraulicCircuit 4 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2642 |  | HydraulicCircuit 4 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 2643 |  | HydraulicCircuit 4 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 2644 |  | HydraulicCircuit 4 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 2645 |  | HydraulicCircuit 4 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 2646 |  | HydraulicCircuit 4 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 2651 |  | HydraulicCircuit 5 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2652 |  | HydraulicCircuit 5 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2653 |  | HydraulicCircuit 5 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2654 |  | HydraulicCircuit 5 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2655 |  | HydraulicCircuit 5 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 2656 |  | HydraulicCircuit 5 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 2657 |  | HydraulicCircuit 5 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 2658 |  | HydraulicCircuit 5 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 2659 |  | HydraulicCircuit 5 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 2664 |  | HydraulicCircuit 6 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2665 |  | HydraulicCircuit 6 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2666 |  | HydraulicCircuit 6 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2667 |  | HydraulicCircuit 6 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2668 |  | HydraulicCircuit 6 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 2669 |  | HydraulicCircuit 6 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 2670 |  | HydraulicCircuit 6 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 2671 |  | HydraulicCircuit 6 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 2672 |  | HydraulicCircuit 6 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 2677 |  | HydraulicCircuit 7 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2678 |  | HydraulicCircuit 7 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2679 |  | HydraulicCircuit 7 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2680 |  | HydraulicCircuit 7 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2681 |  | HydraulicCircuit 7 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 2682 |  | HydraulicCircuit 7 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 2683 |  | HydraulicCircuit 7 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 2684 |  | HydraulicCircuit 7 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 2685 |  | HydraulicCircuit 7 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 2690 |  | HydraulicCircuit 8 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2691 |  | HydraulicCircuit 8 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2692 |  | HydraulicCircuit 8 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2693 |  | HydraulicCircuit 8 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2694 |  | HydraulicCircuit 8 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 2695 |  | HydraulicCircuit 8 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 2696 |  | HydraulicCircuit 8 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 2697 |  | HydraulicCircuit 8 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 2698 |  | HydraulicCircuit 8 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 2703 |  | i2c | Global Error State | 0 | 4 | 0-No_Error 1-i2c_driver_error 2-Wrong_Cycle_Time 3-Missing_Module_Slot 4-Module_Slot_Error |  | int
INPUT_REGISTER | Read | 2704 |  | i2c | Slot1 Module Detected |  |  | 0-Unknown 1-None 22-FM_CM 25-FM_SI 28-FM_MM 29-FM_MW 30-FM_AM 31-FM_CM2 |  | int
INPUT_REGISTER | Read | 2705 |  | i2c | Slot1 Error State |  |  | 0-No_Error 1-No_Response 2-Wrong_Module 3-Unsupported_Module 4-Internal_Sw_Error 5-Communication_Failed 6-Internal_Module_Error 7-Module_Not_Supported_Current_Variant 8-Module_Not_Suppported_In_Slot 9-Module_Count_Too_High 10-Module_Not_Supported_With_Connected_Boiler_Type |  | int
INPUT_REGISTER | Read | 2706 |  | i2c | Slot2 Module Detected |  |  | 0-Unknown 1-None 22-FM_CM 25-FM_SI 28-FM_MM 29-FM_MW 30-FM_AM 31-FM_CM2 |  | int
INPUT_REGISTER | Read | 2707 |  | i2c | Slot2 Error State |  |  | 0-No_Error 1-No_Response 2-Wrong_Module 3-Unsupported_Module 4-Internal_Sw_Error 5-Communication_Failed 6-Internal_Module_Error 7-Module_Not_Supported_Current_Variant 8-Module_Not_Suppported_In_Slot 9-Module_Count_Too_High 10-Module_Not_Supported_With_Connected_Boiler_Type |  | int
INPUT_REGISTER | Read | 2708 |  | i2c | Slot3 Module Detected |  |  | 0-Unknown 1-None 22-FM_CM 25-FM_SI 28-FM_MM 29-FM_MW 30-FM_AM 31-FM_CM2 |  | int
INPUT_REGISTER | Read | 2709 |  | i2c | Slot3 Error State |  |  | 0-No_Error 1-No_Response 2-Wrong_Module 3-Unsupported_Module 4-Internal_Sw_Error 5-Communication_Failed 6-Internal_Module_Error 7-Module_Not_Supported_Current_Variant 8-Module_Not_Suppported_In_Slot 9-Module_Count_Too_High 10-Module_Not_Supported_With_Connected_Boiler_Type |  | int
INPUT_REGISTER | Read | 2710 |  | i2c | Slot4 Module Detected |  |  | 0-Unknown 1-None 22-FM_CM 25-FM_SI 28-FM_MM 29-FM_MW 30-FM_AM 31-FM_CM2 |  | int
INPUT_REGISTER | Read | 2711 |  | i2c | Slot4 Error State |  |  | 0-No_Error 1-No_Response 2-Wrong_Module 3-Unsupported_Module 4-Internal_Sw_Error 5-Communication_Failed 6-Internal_Module_Error 7-Module_Not_Supported_Current_Variant 8-Module_Not_Suppported_In_Slot 9-Module_Count_Too_High 10-Module_Not_Supported_With_Connected_Boiler_Type |  | int
INPUT_REGISTER | Read | 2712 |  | i2c | Slot A Module Detected |  |  | 0-Unknown 1-None 26-ZM5313 27-ZM5311 |  | int
INPUT_REGISTER | Read | 2713 |  | i2c | Slot A Error State |  |  | 0-No_Error 1-No_Response 2-Wrong_Module 3-Unsupported_Module 4-Internal_Sw_Error 5-Communication_Failed 6-Internal_Module_Error 7-Module_Not_Supported_Current_Variant 8-Module_Not_Suppported_In_Slot 9-Module_Count_Too_High 10-Module_Not_Supported_With_Connected_Boiler_Type |  | int
INPUT_REGISTER | Read | 2714 |  | i2c | irBitblock |  |  |  |  | int
| Read |  | 0 | i2c | Component Error |  |  |  |  | bit
INPUT_REGISTER | Read | 2725 |  | fm-si | irBitblock |  |  |  |  | int
| Read |  | 0 | fm-si | Input 1 Error |  |  |  |  | bit
| Read |  | 1 | fm-si | Input 2 Error |  |  |  |  | bit
| Read |  | 2 | fm-si | Input 3 Error |  |  |  |  | bit
| Read |  | 3 | fm-si | Input 4 Error |  |  |  |  | bit
| Read |  | 4 | fm-si | Input 5 Error |  |  |  |  | bit
INPUT_REGISTER | Read | 2732 |  | Sdc | Demand Mode (Low Priority) | 0 | 2 | 0-Off 1-Take_Heat 2-Give_Heat |  | int
INPUT_REGISTER | Read | 2733 |  | Sdc | Demand Flow Temp (Low Priority) |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2734 |  | Sdc | Demand Mode (High Priority) | 0 | 2 | 0-Off 1-Take_Heat 2-Give_Heat |  | int
INPUT_REGISTER | Read | 2735 |  | Sdc | Demand Flow Temp (High Priority) |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2739 |  | Heat Pump | System return temperature for HP heating buffer |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2740 |  | Heat Pump | Buffer mid temperature for HP heating buffer |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2741 |  | Heat Pump | Buffer top temperature for HP heating buffer |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2742 |  | Heat Pump | Buffer bottom temperature for HP heating buffer |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2743 |  | Heat Pump | Return temperature FWR |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2744 |  | Heat Pump | Flow temperature FWV |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2745 |  | Heat Pump | Flow temperature HP |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2746 |  | Heat Pump | Return temperature HP |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2747 |  | Heat Pump | HMI State of HP Component | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 2748 |  | Heat Pump | HP current heat output |  |  |  | kW | signed int | x10
INPUT_REGISTER | Read | 2749 |  | Heat Pump | HP current electrical power consumption | 0 | 10000 |  | kW | int | x10
INPUT_REGISTER | Read | 2750 |  | Heat Pump | HP Smart grid mode | 0 | 3 | 0-normal_charging_grid 1-low_charging_grid 2-high_charging_grid 3-free_charging_grid |  | int
INPUT_REGISTER | Read | 2751 |  | Heat Pump | Heat demand temperature set point |  |  |  | °C | int
INPUT_REGISTER | Read | 2752 |  | Heat Pump | heatPumpStatusIrBitblock | 0 |  |  |  | int
INPUT_REGISTER | Read | 2753 |  | Heat Pump | Ambient Temperature HP |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2754 |  | Heat Pump | HP silent mode | 0 | 3 | 0-standard_mode 1-silent_mode 2-super_silent_mode 3-night_mode |  | int
INPUT_REGISTER | Read | 2755 |  | Heat Pump | Heat Pump Heat Request Temperature |  |  |  | °C | int
INPUT_REGISTER | Read | 2756 |  | Heat Pump | heatPumpIrBitblock |  |  |  |  | int
INPUT_REGISTER | Read | 2765 |  | System | Open Notifications Count |  |  |  |  | int
INPUT_REGISTER | Read | 2766 |  | System | Error Key 5 |  |  |  |  | long
INPUT_REGISTER | Read | 2768 |  | System | Error Key 6 |  |  |  |  | long
INPUT_REGISTER | Read | 2770 |  | System | Error Key 7 |  |  |  |  | long
INPUT_REGISTER | Read | 2772 |  | System | Error Key 8 |  |  |  |  | long
INPUT_REGISTER | Read | 2774 |  | System | Error Key 9 |  |  |  |  | long
INPUT_REGISTER | Read | 2776 |  | System | Error Key 10 |  |  |  |  | long
INPUT_REGISTER | Read | 2778 |  | Chp / EC Power | Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2779 |  | Chp / EC Power | Return Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2780 |  | Chp | Flue Gas Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2781 |  | Chp | Motor Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2782 |  | Chp / EC Power | Current Generator Power |  |  |  | kW | int
INPUT_REGISTER | Read | 2783 |  | Chp | Current Power Setpoint |  |  |  | kW | int
INPUT_REGISTER | Read | 2784 |  | Chp / EC Power | Operation Hours |  |  |  | h | long
INPUT_REGISTER | Read | 2786 |  | Chp / EC Power | Number of starts |  |  |  |  | long
INPUT_REGISTER | Read | 2788 |  | Chp / EC Power | Hours to Maintenance |  |  |  | h | int
INPUT_REGISTER | Read | 2790 |  | Chp | Output Power Setpoint |  |  |  | kW | int
INPUT_REGISTER | Read | 2791 |  | Chp | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 2796 |  | Chp | irBitblock |  |  |  |  | int
| Read |  | 0 | Chp | Warning |  |  |  |  | bit
| Read |  | 1 | Chp / EC Power | Malfunction |  |  |  |  | bit
| Read |  | 2 | Chp / EC Power | Controlled Shutdown |  |  |  |  | bit
| Read |  | 3 | Chp / EC Power | Generator On |  |  |  |  | bit
| Read |  | 4 | Chp | Automatic On |  |  |  |  | bit
| Read |  | 5 | Chp / EC Power | Automatic Ready |  |  |  |  | bit
| Read |  | 11 | Chp / EC Power | Output On Request |  |  |  |  | bit
INPUT_REGISTER | Read | 2804 |  | Water Treatment Module | Program Step |  |  | 20-140: Desalination not active 10000-10810: One time desalination 20000-20810: Automatic desalination 30000-30260: Stationary operation |  | int
INPUT_REGISTER | Read | 2805 |  | Water Treatment Module | Temperature Desalinization |  |  |  | °C | int | x10
INPUT_REGISTER | Read | 2806 |  | Water Treatment Module | Volume Flow |  |  |  | L/min | int | x10
INPUT_REGISTER | Read | 2807 |  | Water Treatment Module | Conductivity system |  |  |  | uS/cm | int | x10
INPUT_REGISTER | Read | 2808 |  | Water Treatment Module | Conductivity cartridge |  |  |  | uS/cm | int | x10
INPUT_REGISTER | Read | 2809 |  | Water Treatment Module | Cartridge Capacity |  |  |  | % | int
INPUT_REGISTER | Read | 2813 |  | Solar Data | Collector temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2814 |  | Solar Data | Temperature cylinder bottom |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2815 |  | Solar Data | Solar pump modulation setpoint |  |  |  | % | int
INPUT_REGISTER | Read | 2816 |  | Solar | Solar pump status | 0 | 19 | 1-TestMod 2-BlckProt 3-No heat 4-Ht avail 5-SolOff 6-MaxCyl 7-MaxColl 8-MinColl 9-FrostP 10-VacFct 11-SwChck 12-MixPrio 13-Switch 14-Priority 15-ThermD 16-MixCal 17-MixOpn 18-MixCl 19-MixOff |  | int
INPUT_REGISTER | Read | 2817 |  | Solar Data | Heat exchanger temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2818 |  | Solar Data | Heat exchanger pump modulation setpoint |  |  |  | % | int
INPUT_REGISTER | Read | 2819 |  | Solar | Heat exchanger pump status | 0 | 19 | 1-TestMod 2-BlckProt 3-No heat 4-Ht avail 5-SolOff 6-MaxCyl 7-MaxColl 8-MinColl 9-FrostP 10-VacFct 11-SwChck 12-MixPrio 13-Switch 14-Priority 15-ThermD 16-MixCal 17-MixOpn 18-MixCl 19-MixOff |  | int
INPUT_REGISTER | Read | 2820 |  | Solar Data | Temperature cylinder 3 top |  |  |  | °C | int | x10
INPUT_REGISTER | Read | 2821 |  | Solar Data | Reload pump modulation setpoint |  |  |  | % | int
INPUT_REGISTER | Read | 2822 |  | Solar | Reload pump status | 0 | 19 | 1-TestMod 2-BlckProt 3-No heat 4-Ht avail 5-SolOff 6-MaxCyl 7-MaxColl 8-MinColl 9-FrostP 10-VacFct 11-SwChck 12-MixPrio 13-Switch 14-Priority 15-ThermD 16-MixCal 17-MixOpn 18-MixCl 19-MixOff |  | int
INPUT_REGISTER | Read | 2823 |  | Solar | Pump therm. disinfect. status | 0 | 19 | 1-TestMod 2-BlckProt 3-No heat 4-Ht avail 5-SolOff 6-MaxCyl 7-MaxColl 8-MinColl 9-FrostP 10-VacFct 11-SwChck 12-MixPrio 13-Switch 14-Priority 15-ThermD 16-MixCal 17-MixOpn 18-MixCl 19-MixOff |  | int
INPUT_REGISTER | Read | 2824 |  | Solar Yield | Flow temperature heat meter |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2825 |  | Solar Yield | Return temperature heat meter |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2826 |  | Solar Yield | Heat count pulse counter | 0 | 15 |  |  | int
INPUT_REGISTER | Read | 2827 |  | Solar Yield | Solar yield per month |  |  |  | kWh | long | x10
INPUT_REGISTER | Read | 2829 |  | Solar Yield | Solar yield per year |  |  |  | kWh | long | x10
INPUT_REGISTER | Read | 2831 |  | Solar Yield | Last hour solar yield |  |  |  | kWh | long | x10
INPUT_REGISTER | Read | 2833 |  | Solar Yield | Solar yield per day |  |  |  | kWh | long | x10
INPUT_REGISTER | Read | 2835 |  | Solar Yield | Solar yield since installation |  |  |  | kWh | long | x10
INPUT_REGISTER | Read | 2837 |  | Solar | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 2838 |  | Solar Data | Hydraulic configuration |  |  |  |  | int
| Read |  | 0 | Solar | Option 1 active |  |  |  |  | bit
| Read |  | 1 | Solar | Option A active |  |  |  |  | bit
| Read |  | 2 | Solar | Option B active |  |  |  |  | bit
| Read |  | 3 | Solar | Option C active |  |  |  |  | bit
| Read |  | 4 | Solar | Option D active |  |  |  |  | bit
| Read |  | 5 | Solar | Option E active |  |  |  |  | bit
| Read |  | 6 | Solar | Option F active |  |  |  |  | bit
| Read |  | 7 | Solar | Option G active |  |  |  |  | bit
| Read |  | 8 | Solar | Option H active |  |  |  |  | bit
| Read |  | 9 | Solar | Option I active |  |  |  |  | bit
| Read |  | 10 | Solar | Option J active |  |  |  |  | bit
| Read |  | 11 | Solar | Option K active |  |  |  |  | bit
| Read |  | 12 | Solar | Option L active |  |  |  |  | bit
| Read |  | 13 | Solar | Option M active |  |  |  |  | bit
| Read |  | 14 | Solar | Option N active |  |  |  |  | bit
| Read |  | 15 | Solar | Option P active |  |  |  |  | bit
INPUT_REGISTER | Read | 2839 |  | Solar Data | irBitblock |  |  |  |  | int
| Read |  | 0 | Solar | Is Active |  |  |  |  | bit
INPUT_REGISTER |  | 2900 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 2901 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 2902 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 2903 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 2904 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 2905 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 2906 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 2907 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 2908 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 2909 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 2910 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 2911 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 2912 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 2913 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER | Read | 2922 |  | Energy Monitoring | Heat Output |  |  |  | kW | signed int | x10
INPUT_REGISTER | Read | 2923 |  | Energy Monitoring | Gas Consumption (LCV) |  |  |  | kW | signed int | x10
INPUT_REGISTER | Read | 2925 |  | Energy Monitoring | Electrical Power |  |  |  | W | int
INPUT_REGISTER | Read | 2930 |  | Fresh Water Characteristics 1 | DHW Out Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2931 |  | Fresh Water Characteristics 1 | DHW Volume Flow |  |  |  | L/min | signed int | x10
INPUT_REGISTER | Read | 2932 |  | Fresh Water Characteristics 1 | Prim In Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2933 |  | Fresh Water Characteristics 1 | DHW In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2934 |  | Fresh Water Characteristics 1 | Primary Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 2935 |  | Fresh Water Characteristics 1 | Request DHW Out Temperature |  |  |  | °C | int
INPUT_REGISTER | Read | 2936 |  | Fresh Water Characteristics 1 | Status Request DHW Out Temperature | 0 | 9 | 0-Off 1-DHWRed 2-DHW 3-Sol_red 4-Once_on 5-Therm_d 6-DlyHtUp 7-Preheat_start 8-Preheat_normal 9-No_eq |  | int
INPUT_REGISTER | Read | 2937 |  | Fresh Water Characteristics 2 | Circulation Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 2938 |  | Fresh Water Characteristics 2 | Status Circulation Pump | 0 | 8 | 0-Undefined 1-Test 2-BlckProt 3-No_req 4-AutoOff 5-AutoOn 6-Therm_d 7-Sys_Off 8-DlyHtUp |  | int
INPUT_REGISTER | Read | 2939 |  | Fresh Water Characteristics 2 | Return Valve Modulation Request |  |  |  | % | int
INPUT_REGISTER | Read | 2940 |  | Fresh Water Characteristics 2 | Valve State | 0 | 5 | 0-Undefined 1-TestMod 2-BlckProt 3-Mix_cl 4-Mix_opn 5-Sys_Off |  | int
INPUT_REGISTER | Read | 2941 |  | Fresh Water Characteristics 2 | Return Valve Buffer Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2942 |  | Fresh Water Characteristics 2 | Disinfection Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 2943 |  | Fresh Water Characteristics 2 | Pump State | 0 | 5 | 0-Undefined 1-TestMod 2-BlckPro 3-No_eq 4-Ht_req 5-Sys_Off |  | int
INPUT_REGISTER | Read | 2944 |  | Fresh Water Characteristics 1 | DHW Valve Power |  |  |  | % | int
INPUT_REGISTER | Read | 2945 |  | Fresh Water Characteristics 2 | Total Flow |  |  |  | L/min | int | x10
INPUT_REGISTER | Read | 2946 |  | Fresh Water 2 | Module 2 DHW Out Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2947 |  | Fresh Water 2 | Module 2 DHW Volume Flow |  |  |  | L/min | signed int | x10
INPUT_REGISTER | Read | 2948 |  | Fresh Water 2 | Module 2 Prim In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2949 |  | Fresh Water 2 | Module 2 DHW In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2950 |  | Fresh Water 2 | Module 2 DHW Valve Power |  |  |  | % | int
INPUT_REGISTER | Read | 2951 |  | Fresh Water 2 | Module 2 Prim Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 2952 |  | Fresh Water 2 | Module 2 Status Prim Pump |  |  |  |  | int
INPUT_REGISTER | Read | 2953 |  | Fresh Water 3 | Module 3 DHW Out Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2954 |  | Fresh Water 3 | Module 3 DHW Volume Flow |  |  |  | L/min | signed int | x10
INPUT_REGISTER | Read | 2955 |  | Fresh Water 3 | Module 3 Prim In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2956 |  | Fresh Water 3 | Module 3 DHW In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2957 |  | Fresh Water 3 | Module 3 DHW Valve Power |  |  |  | % | int
INPUT_REGISTER | Read | 2958 |  | Fresh Water 3 | Module 3 Prim Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 2959 |  | Fresh Water 3 | Module 3 Status Prim Pump |  |  |  |  | int
INPUT_REGISTER | Read | 2960 |  | Fresh Water 4 | Module 4 DHW Out Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2961 |  | Fresh Water 4 | Module 4 DHW Volume Flow |  |  |  | L/min | signed int | x10
INPUT_REGISTER | Read | 2962 |  | Fresh Water 4 | Module 4 Prim In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2963 |  | Fresh Water 4 | Module 4 DHW In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 2964 |  | Fresh Water 4 | Module 4 DHW ValvePower |  |  |  | % | int
INPUT_REGISTER | Read | 2965 |  | Fresh Water 4 | Module 4 Prim Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 2966 |  | Fresh Water 4 | Module 4 Status Primary Pump |  |  |  |  | int
INPUT_REGISTER | Read | 2967 |  | Fresh Water | Fresh Water Hmi State |  |  |  |  | int
INPUT_REGISTER | Read | 2968 |  | Fresh Water Characteristics 3 | Fresh Water Configurations |  |  |  |  | int
| Read |  | 0 | Fresh Water | Option 2 active |  |  |  |  | bit
| Read |  | 1 | Fresh Water | Option A active |  |  |  |  | bit
| Read |  | 2 | Fresh Water | Option B active |  |  |  |  | bit
| Read |  | 3 | Fresh Water | Option C active |  |  |  |  | bit
| Read |  | 4 | Fresh Water | Option D active |  |  |  |  | bit
| Read |  | 5 | Fresh Water | Option E active |  |  |  |  | bit
| Read |  | 6 | Fresh Water | Option E active cascade module 2 active |  |  |  |  | bit
| Read |  | 7 | Fresh Water | Option E active cascade module 3 active |  |  |  |  | bit
| Read |  | 8 | Fresh Water | Option E active cascade module 4 active |  |  |  |  | bit
| Read |  | 9 | Fresh Water | Is Active |  |  |  |  | bit
INPUT_REGISTER | Read | 2976 |  | System | Error Key 1 |  |  |  |  | long
INPUT_REGISTER | Read | 2978 |  | System | Error Key 2 |  |  |  |  | long
INPUT_REGISTER | Read | 2980 |  | System | Error Key 3 |  |  |  |  | long
INPUT_REGISTER | Read | 2982 |  | System | Error Key 4 |  |  |  |  | long
INPUT_REGISTER | Read | 2984 |  | System | Error 1 Extra Info (MSB) |  |  |  |  | long
INPUT_REGISTER | Read | 2986 |  | System | Error 1 Extra Info (LSB) |  |  |  |  | long
INPUT_REGISTER | Read | 2988 |  | System | Error 2 Extra Info (MSB) |  |  |  |  | long
INPUT_REGISTER | Read | 2990 |  | System | Error 2 Extra Info (LSB) |  |  |  |  | long
INPUT_REGISTER | Read | 2992 |  | System | Error 3 Extra Info (MSB) |  |  |  |  | long
INPUT_REGISTER | Read | 2994 |  | System | Error 3 Extra Info (LSB) |  |  |  |  | long
INPUT_REGISTER | Read | 2996 |  | System | Error 4 Extra Info (MSB) |  |  |  |  | long
INPUT_REGISTER | Read | 2998 |  | System | Error 4 Extra Info (LSB) |  |  |  |  | long

## Slave06
Register Type | Permissions | Address | Bitblock Bit | Component | Name | Min | Max | Range | Unit | DataType | Float to Int Factor
HOLDING_REGISTER | Write | 3007 |  | DomesticHotWater Zm/Ems | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 3008 |  | DomesticHotWater Zm/Ems | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 3009 |  | DomesticHotWater Zm/Ems | Thermal Disinfection Setpoint | 65 | 75 |  | °C | int | x10
HOLDING_REGISTER | Write | 3010 |  | DomesticHotWater Zm | Setpoint Auto Day | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 3011 |  | DomesticHotWater Zm | Setpoint Auto Night | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 3012 |  | DomesticHotWater Zm | Setpoint Manual Day | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 3013 |  | DomesticHotWater Zm | Setpoint Manual Night | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 3014 |  | DomesticHotWater Zm | Setpoint Holiday | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 3015 |  | DomesticHotWater Zm/Ems | Circulation Pump Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 3016 |  | DomesticHotWater Zm/Ems | Circulation Pump Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 3017 |  | DomesticHotWater Zm/Ems | Disinfection Frequency | 0 | 7 | 0-Daily 1-Monday 2-Tuesday 3-Wednesday 4-Thursday 5-Friday 6-Saturday 7-Sunday |  | int
HOLDING_REGISTER | Write | 3018 |  | DomesticHotWater Zm/Ems | Disinfection Start Hour | 0 | 23 |  | h | int
HOLDING_REGISTER | Write | 3021 |  | DomesticHotWater Fm | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 3022 |  | DomesticHotWater Fm | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 3023 |  | DomesticHotWater Fm | Thermal Disinfection Setpoint | 65 | 75 |  | °C | int | x10
HOLDING_REGISTER | Write | 3024 |  | DomesticHotWater Fm | Setpoint Auto Day | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 3025 |  | DomesticHotWater Fm | Setpoint Auto Night | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 3026 |  | DomesticHotWater Fm | Setpoint Manual Day | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 3027 |  | DomesticHotWater Fm | Setpoint Manual Night | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 3028 |  | DomesticHotWater Fm | Setpoint Holiday | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 3029 |  | DomesticHotWater Fm | Circulation Pump Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 3030 |  | DomesticHotWater Fm | Circulation Pump Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 3031 |  | DomesticHotWater Fm | Disinfection Frequency | 0 | 7 | 0-Daily 1-Monday 2-Tuesday 3-Wednesday 4-Thursday 5-Friday 6-Saturday 7-Sunday |  | int
HOLDING_REGISTER | Write | 3032 |  | DomesticHotWater Fm | Disinfection Start Hour | 0 | 23 |  | h | int
HOLDING_REGISTER | Read | 3039 |  | Boiler | Control Type | 0 | 4 | 0-None 1-Safe 2-Ems 3-7Pole 4-Substation |  | int
HOLDING_REGISTER | Write | 3043 |  | AlternativeHeatSource | Operation Mode Request Auto Day | 20 | 99 |  | °C | int
HOLDING_REGISTER | Write | 3044 |  | AlternativeHeatSource | Operation Mode Request Auto Night | 20 | 99 |  | °C | int
HOLDING_REGISTER | Write | 3045 |  | AlternativeHeatSource | Operation Mode Request Manual Day | 20 | 99 |  | °C | int
HOLDING_REGISTER | Write | 3046 |  | AlternativeHeatSource | Operation Mode Request Manual Night | 20 | 99 |  | °C | int
HOLDING_REGISTER | Write | 3047 |  | AlternativeHeatSource | Operation Mode Request Holiday | 20 | 99 |  | °C | int
HOLDING_REGISTER | Write | 3048 |  | AlternativeHeatSource | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 3049 |  | AlternativeHeatSource | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 3050 |  | AlternativeHeatSource | Return Control Setpoint User | 10 | 70 |  | °C | int
HOLDING_REGISTER | Write | 3057 |  | HydraulicCircuit Zm | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 3058 |  | HydraulicCircuit Zm | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 3059 |  | HydraulicCircuit Zm | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3060 |  | HydraulicCircuit Zm | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3061 |  | HydraulicCircuit Zm | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3062 |  | HydraulicCircuit Zm | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3063 |  | HydraulicCircuit Zm | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3064 |  | HydraulicCircuit Zm | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 3070 |  | HydraulicCircuit 1 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 3071 |  | HydraulicCircuit 1 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 3072 |  | HydraulicCircuit 1 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3073 |  | HydraulicCircuit 1 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3074 |  | HydraulicCircuit 1 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3075 |  | HydraulicCircuit 1 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3076 |  | HydraulicCircuit 1 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3077 |  | HydraulicCircuit 1 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 3083 |  | HydraulicCircuit 2 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 3084 |  | HydraulicCircuit 2 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 3085 |  | HydraulicCircuit 2 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3086 |  | HydraulicCircuit 2 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3087 |  | HydraulicCircuit 2 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3088 |  | HydraulicCircuit 2 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3089 |  | HydraulicCircuit 2 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3090 |  | HydraulicCircuit 2 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 3096 |  | HydraulicCircuit 3 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 3097 |  | HydraulicCircuit 3 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 3098 |  | HydraulicCircuit 3 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3099 |  | HydraulicCircuit 3 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3100 |  | HydraulicCircuit 3 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3101 |  | HydraulicCircuit 3 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3102 |  | HydraulicCircuit 3 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3103 |  | HydraulicCircuit 3 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 3109 |  | HydraulicCircuit 4 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 3110 |  | HydraulicCircuit 4 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 3111 |  | HydraulicCircuit 4 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3112 |  | HydraulicCircuit 4 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3113 |  | HydraulicCircuit 4 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3114 |  | HydraulicCircuit 4 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3115 |  | HydraulicCircuit 4 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3116 |  | HydraulicCircuit 4 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 3122 |  | HydraulicCircuit 5 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 3123 |  | HydraulicCircuit 5 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 3124 |  | HydraulicCircuit 5 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3125 |  | HydraulicCircuit 5 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3126 |  | HydraulicCircuit 5 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3127 |  | HydraulicCircuit 5 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3128 |  | HydraulicCircuit 5 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3129 |  | HydraulicCircuit 5 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 3135 |  | HydraulicCircuit 6 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 3136 |  | HydraulicCircuit 6 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 3137 |  | HydraulicCircuit 6 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3138 |  | HydraulicCircuit 6 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3139 |  | HydraulicCircuit 6 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3140 |  | HydraulicCircuit 6 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3141 |  | HydraulicCircuit 6 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3142 |  | HydraulicCircuit 6 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 3148 |  | HydraulicCircuit 7 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 3149 |  | HydraulicCircuit 7 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 3150 |  | HydraulicCircuit 7 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3151 |  | HydraulicCircuit 7 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3152 |  | HydraulicCircuit 7 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3153 |  | HydraulicCircuit 7 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3154 |  | HydraulicCircuit 7 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3155 |  | HydraulicCircuit 7 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 3161 |  | HydraulicCircuit 8 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 3162 |  | HydraulicCircuit 8 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 3163 |  | HydraulicCircuit 8 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3164 |  | HydraulicCircuit 8 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3165 |  | HydraulicCircuit 8 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3166 |  | HydraulicCircuit 8 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3167 |  | HydraulicCircuit 8 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3168 |  | HydraulicCircuit 8 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 3201 |  | Heat Pump | Heat demand source | 0 | 2 | 0-Scheduler 1-System 2-Max_system_scheduler |  | int
HOLDING_REGISTER | Read | 3421 |  | Fresh Water Characteristics 3 | DHU Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 3422 |  | Fresh Water Characteristics 3 | Extra Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 3423 |  | Fresh Water Characteristics 3 | Maximum DHW Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 3424 |  | Fresh Water Characteristics 3 | On High Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 3425 |  | Fresh Water Characteristics 3 | On Low Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 3426 |  | Fresh Water Characteristics 3 | Fresh Water Type | 0 | 3 | 0-15/20l/min 1-27l/min 2-40l/min 3-60l/min |  | int
HOLDING_REGISTER | Read | 3427 |  | Fresh Water Characteristics 3 | Enable Alarm Output | 0 | 2 | 0-No 1-Yes 2-Inverted |  | int
HOLDING_REGISTER | Read | 3428 |  | Fresh Water Characteristics 3 | Buffer Cylinder Temperature Offset |  |  |  | K | int
HOLDING_REGISTER | Read | 3429 |  | Fresh Water Characteristics 3 | hrBitblock |  |  |  |  | int
| Read |  | 0 | Fresh Water | Buffer Cylinder Temperature Optimization Enabled |  |  |  |  | bit
| Read |  | 1 | Fresh Water | Impulse Enabled |  |  |  |  | bit
| Read |  | 2 | Fresh Water | Time Program Enabled |  |  |  |  | bit
HOLDING_REGISTER | Read | 3430 |  | Fresh Water Characteristics 3 | Minimum Buffer Cylinder Temperature Offset |  |  |  | K | int
HOLDING_REGISTER | Read | 3431 |  | Fresh Water Characteristics 2 | Circulation Pump Runs per Hour | 0 | 7 | 0-Undefined 1-1x3_minutes/h 2-2x3_minutes/h 3-3x3_minutes/h 4-4x3_minutes/h 5-5x3_minutes/h 6-6x3_minutes/h 7-Permanent |  | int
HOLDING_REGISTER | Read | 3432 |  | Fresh Water Characteristics 2 | Swich Hysteresis |  |  |  | K | int
HOLDING_REGISTER | Read | 3433 |  | Fresh Water Characteristics 2 | Thermal Disinfection Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 3434 |  | Fresh Water Characteristics 2 | Pre Heat Maximum Temperature |  |  |  | °C | int
INPUT_REGISTER | Read | 3000 |  | System | Own Outdoor temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3001 |  | System | Damped Own outdoor temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3004 |  | System | Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3008 |  | System | Active Functions 1 |  |  |  |  | int
INPUT_REGISTER | Read | 3009 |  | System | Active Functions 2 |  |  |  |  | int
INPUT_REGISTER | Read | 3015 |  | DomesticHotWater Zm | Charge Pump Running | 0 | 4 | 0-Stopping 1-Starting 2-Running 3-Off 4-Error |  | int
INPUT_REGISTER | Read | 3016 |  | DomesticHotWater Zm | Circulation Pump Running | 0 | 4 | 0-Stopping 1-Starting 2-Running 3-Off 4-Error |  | int
INPUT_REGISTER | Read | 3017 |  | DomesticHotWater Zm | Hydraulic State | 0 | 7 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Cold_load 6-Post_purge 7-Condense_protection |  | int
INPUT_REGISTER | Read | 3018 |  | DomesticHotWater Zm/Ems | Thermal Disinfection Status | 0 | 3 | 0-Off 1-On 2-Success 3-Error |  | int
INPUT_REGISTER | Read | 3019 |  | DomesticHotWater Zm/Ems | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 3020 |  | DomesticHotWater Zm/Ems | Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3021 |  | DomesticHotWater Zm/Ems | Current Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3031 |  | DomesticHotWater Fm | Charge Pump Running | 0 | 4 | 0-Stopping 1-Starting 2-Running 3-Off 4-Error |  | int
INPUT_REGISTER | Read | 3032 |  | DomesticHotWater Fm | Circulation Pump Running | 0 | 4 | 0-Stopping 1-Starting 2-Running 3-Off 4-Error |  | int
INPUT_REGISTER | Read | 3033 |  | DomesticHotWater Fm | Hydraulic State | 0 | 7 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Cold_load 6-Post_purge 7-Condense_protection |  | int
INPUT_REGISTER | Read | 3034 |  | DomesticHotWater Fm | Thermal Disinfection Status | 0 | 3 | 0-Off 1-On 2-Success 3-Error |  | int
INPUT_REGISTER | Read | 3035 |  | DomesticHotWater Fm | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 3036 |  | DomesticHotWater Fm | Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3037 |  | DomesticHotWater Fm | Current Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER |  | 3047 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 3048 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 3050 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 3052 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 3053 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 3054 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 3055 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 3056 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 3059 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 3060 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER | Read | 3063 |  | AlternativeHeatSource | Operating hours |  |  |  | h | long
INPUT_REGISTER | Read | 3065 |  | AlternativeHeatSource | Heat Source Starts |  |  |  |  | long
INPUT_REGISTER | Read | 3067 |  | AlternativeHeatSource | Heat Source Hours to Maintenance |  |  |  | h | int
INPUT_REGISTER | Read | 3069 |  | AlternativeHeatSource | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
| Read |  | 0 | AlternativeHeatSource | Is Heat Source On |  |  |  |  | bit
| Read |  | 1 | AlternativeHeatSource | Is Heat Source On Request |  |  |  |  | bit
INPUT_REGISTER | Read | 3087 |  | HydraulicCircuit Zm | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3088 |  | HydraulicCircuit Zm | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3089 |  | HydraulicCircuit Zm | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3090 |  | HydraulicCircuit Zm | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3091 |  | HydraulicCircuit Zm | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 3092 |  | HydraulicCircuit Zm | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 3093 |  | HydraulicCircuit Zm | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 3094 |  | HydraulicCircuit Zm | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 3095 |  | HydraulicCircuit Zm | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 3099 |  | HydraulicCircuit 1 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3100 |  | HydraulicCircuit 1 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3101 |  | HydraulicCircuit 1 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3102 |  | HydraulicCircuit 1 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3103 |  | HydraulicCircuit 1 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 3104 |  | HydraulicCircuit 1 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 3105 |  | HydraulicCircuit 1 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 3106 |  | HydraulicCircuit 1 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 3107 |  | HydraulicCircuit 1 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 3112 |  | HydraulicCircuit 2 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3113 |  | HydraulicCircuit 2 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3114 |  | HydraulicCircuit 2 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3115 |  | HydraulicCircuit 2 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3116 |  | HydraulicCircuit 2 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 3117 |  | HydraulicCircuit 2 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 3118 |  | HydraulicCircuit 2 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 3119 |  | HydraulicCircuit 2 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 3120 |  | HydraulicCircuit 2 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 3125 |  | HydraulicCircuit 3 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3126 |  | HydraulicCircuit 3 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3127 |  | HydraulicCircuit 3 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3128 |  | HydraulicCircuit 3 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3129 |  | HydraulicCircuit 3 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 3130 |  | HydraulicCircuit 3 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 3131 |  | HydraulicCircuit 3 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 3132 |  | HydraulicCircuit 3 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 3133 |  | HydraulicCircuit 3 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 3138 |  | HydraulicCircuit 4 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3139 |  | HydraulicCircuit 4 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3140 |  | HydraulicCircuit 4 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3141 |  | HydraulicCircuit 4 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3142 |  | HydraulicCircuit 4 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 3143 |  | HydraulicCircuit 4 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 3144 |  | HydraulicCircuit 4 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 3145 |  | HydraulicCircuit 4 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 3146 |  | HydraulicCircuit 4 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 3151 |  | HydraulicCircuit 5 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3152 |  | HydraulicCircuit 5 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3153 |  | HydraulicCircuit 5 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3154 |  | HydraulicCircuit 5 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3155 |  | HydraulicCircuit 5 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 3156 |  | HydraulicCircuit 5 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 3157 |  | HydraulicCircuit 5 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 3158 |  | HydraulicCircuit 5 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 3159 |  | HydraulicCircuit 5 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 3164 |  | HydraulicCircuit 6 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3165 |  | HydraulicCircuit 6 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3166 |  | HydraulicCircuit 6 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3167 |  | HydraulicCircuit 6 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3168 |  | HydraulicCircuit 6 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 3169 |  | HydraulicCircuit 6 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 3170 |  | HydraulicCircuit 6 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 3171 |  | HydraulicCircuit 6 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 3172 |  | HydraulicCircuit 6 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 3177 |  | HydraulicCircuit 7 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3178 |  | HydraulicCircuit 7 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3179 |  | HydraulicCircuit 7 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3180 |  | HydraulicCircuit 7 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3181 |  | HydraulicCircuit 7 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 3182 |  | HydraulicCircuit 7 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 3183 |  | HydraulicCircuit 7 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 3184 |  | HydraulicCircuit 7 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 3185 |  | HydraulicCircuit 7 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 3190 |  | HydraulicCircuit 8 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3191 |  | HydraulicCircuit 8 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3192 |  | HydraulicCircuit 8 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3193 |  | HydraulicCircuit 8 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3194 |  | HydraulicCircuit 8 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 3195 |  | HydraulicCircuit 8 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 3196 |  | HydraulicCircuit 8 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 3197 |  | HydraulicCircuit 8 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 3198 |  | HydraulicCircuit 8 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 3203 |  | i2c | Global Error State | 0 | 4 | 0-No_Error 1-i2c_driver_error 2-Wrong_Cycle_Time 3-Missing_Module_Slot 4-Module_Slot_Error |  | int
INPUT_REGISTER | Read | 3204 |  | i2c | Slot1 Module Detected |  |  | 0-Unknown 1-None 22-FM_CM 25-FM_SI 28-FM_MM 29-FM_MW 30-FM_AM 31-FM_CM2 |  | int
INPUT_REGISTER | Read | 3205 |  | i2c | Slot1 Error State |  |  | 0-No_Error 1-No_Response 2-Wrong_Module 3-Unsupported_Module 4-Internal_Sw_Error 5-Communication_Failed 6-Internal_Module_Error 7-Module_Not_Supported_Current_Variant 8-Module_Not_Suppported_In_Slot 9-Module_Count_Too_High 10-Module_Not_Supported_With_Connected_Boiler_Type |  | int
INPUT_REGISTER | Read | 3206 |  | i2c | Slot2 Module Detected |  |  | 0-Unknown 1-None 22-FM_CM 25-FM_SI 28-FM_MM 29-FM_MW 30-FM_AM 31-FM_CM2 |  | int
INPUT_REGISTER | Read | 3207 |  | i2c | Slot2 Error State |  |  | 0-No_Error 1-No_Response 2-Wrong_Module 3-Unsupported_Module 4-Internal_Sw_Error 5-Communication_Failed 6-Internal_Module_Error 7-Module_Not_Supported_Current_Variant 8-Module_Not_Suppported_In_Slot 9-Module_Count_Too_High 10-Module_Not_Supported_With_Connected_Boiler_Type |  | int
INPUT_REGISTER | Read | 3208 |  | i2c | Slot3 Module Detected |  |  | 0-Unknown 1-None 22-FM_CM 25-FM_SI 28-FM_MM 29-FM_MW 30-FM_AM 31-FM_CM2 |  | int
INPUT_REGISTER | Read | 3209 |  | i2c | Slot3 Error State |  |  | 0-No_Error 1-No_Response 2-Wrong_Module 3-Unsupported_Module 4-Internal_Sw_Error 5-Communication_Failed 6-Internal_Module_Error 7-Module_Not_Supported_Current_Variant 8-Module_Not_Suppported_In_Slot 9-Module_Count_Too_High 10-Module_Not_Supported_With_Connected_Boiler_Type |  | int
INPUT_REGISTER | Read | 3210 |  | i2c | Slot4 Module Detected |  |  | 0-Unknown 1-None 22-FM_CM 25-FM_SI 28-FM_MM 29-FM_MW 30-FM_AM 31-FM_CM2 |  | int
INPUT_REGISTER | Read | 3211 |  | i2c | Slot4 Error State |  |  | 0-No_Error 1-No_Response 2-Wrong_Module 3-Unsupported_Module 4-Internal_Sw_Error 5-Communication_Failed 6-Internal_Module_Error 7-Module_Not_Supported_Current_Variant 8-Module_Not_Suppported_In_Slot 9-Module_Count_Too_High 10-Module_Not_Supported_With_Connected_Boiler_Type |  | int
INPUT_REGISTER | Read | 3212 |  | i2c | Slot A Module Detected |  |  | 0-Unknown 1-None 26-ZM5313 27-ZM5311 |  | int
INPUT_REGISTER | Read | 3213 |  | i2c | Slot A Error State |  |  | 0-No_Error 1-No_Response 2-Wrong_Module 3-Unsupported_Module 4-Internal_Sw_Error 5-Communication_Failed 6-Internal_Module_Error 7-Module_Not_Supported_Current_Variant 8-Module_Not_Suppported_In_Slot 9-Module_Count_Too_High 10-Module_Not_Supported_With_Connected_Boiler_Type |  | int
INPUT_REGISTER | Read | 3214 |  | i2c | irBitblock |  |  |  |  | int
| Read |  | 0 | i2c | Component Error |  |  |  |  | bit
INPUT_REGISTER | Read | 3225 |  | fm-si | irBitblock |  |  |  |  | int
| Read |  | 0 | fm-si | Input 1 Error |  |  |  |  | bit
| Read |  | 1 | fm-si | Input 2 Error |  |  |  |  | bit
| Read |  | 2 | fm-si | Input 3 Error |  |  |  |  | bit
| Read |  | 3 | fm-si | Input 4 Error |  |  |  |  | bit
| Read |  | 4 | fm-si | Input 5 Error |  |  |  |  | bit
INPUT_REGISTER | Read | 3232 |  | Sdc | Demand Mode (Low Priority) | 0 | 2 | 0-Off 1-Take_Heat 2-Give_Heat |  | int
INPUT_REGISTER | Read | 3233 |  | Sdc | Demand Flow Temp (Low Priority) |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3234 |  | Sdc | Demand Mode (High Priority) | 0 | 2 | 0-Off 1-Take_Heat 2-Give_Heat |  | int
INPUT_REGISTER | Read | 3235 |  | Sdc | Demand Flow Temp (High Priority) |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3239 |  | Heat Pump | System return temperature for HP heating buffer |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3240 |  | Heat Pump | Buffer mid temperature for HP heating buffer |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3241 |  | Heat Pump | Buffer top temperature for HP heating buffer |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3242 |  | Heat Pump | Buffer bottom temperature for HP heating buffer |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3243 |  | Heat Pump | Return temperature FWR |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3244 |  | Heat Pump | Flow temperature FWV |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3245 |  | Heat Pump | Flow temperature HP |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3246 |  | Heat Pump | Return temperature HP |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3247 |  | Heat Pump | HMI State of HP Component | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 3248 |  | Heat Pump | HP current heat output |  |  |  | kW | signed int | x10
INPUT_REGISTER | Read | 3249 |  | Heat Pump | HP current electrical power consumption | 0 | 10000 |  | kW | int | x10
INPUT_REGISTER | Read | 3250 |  | Heat Pump | HP Smart grid mode | 0 | 3 | 0-normal_charging_grid 1-low_charging_grid 2-high_charging_grid 3-free_charging_grid |  | int
INPUT_REGISTER | Read | 3251 |  | Heat Pump | Heat demand temperature set point |  |  |  | °C | int
INPUT_REGISTER | Read | 3252 |  | Heat Pump | heatPumpStatusIrBitblock | 0 |  |  |  | int
INPUT_REGISTER | Read | 3253 |  | Heat Pump | Ambient Temperature HP |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3254 |  | Heat Pump | HP silent mode | 0 | 3 | 0-standard_mode 1-silent_mode 2-super_silent_mode 3-night_mode |  | int
INPUT_REGISTER | Read | 3255 |  | Heat Pump | Heat Pump Heat Request Temperature |  |  |  | °C | int
INPUT_REGISTER | Read | 3256 |  | Heat Pump | heatPumpIrBitblock |  |  |  |  | int
INPUT_REGISTER | Read | 3265 |  | System | Open Notifications Count |  |  |  |  | int
INPUT_REGISTER | Read | 3266 |  | System | Error Key 5 |  |  |  |  | long
INPUT_REGISTER | Read | 3268 |  | System | Error Key 6 |  |  |  |  | long
INPUT_REGISTER | Read | 3270 |  | System | Error Key 7 |  |  |  |  | long
INPUT_REGISTER | Read | 3272 |  | System | Error Key 8 |  |  |  |  | long
INPUT_REGISTER | Read | 3274 |  | System | Error Key 9 |  |  |  |  | long
INPUT_REGISTER | Read | 3276 |  | System | Error Key 10 |  |  |  |  | long
INPUT_REGISTER | Read | 3278 |  | Chp / EC Power | Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3279 |  | Chp / EC Power | Return Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3280 |  | Chp | Flue Gas Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3281 |  | Chp | Motor Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3282 |  | Chp / EC Power | Current Generator Power |  |  |  | kW | int
INPUT_REGISTER | Read | 3283 |  | Chp | Current Power Setpoint |  |  |  | kW | int
INPUT_REGISTER | Read | 3284 |  | Chp / EC Power | Operation Hours |  |  |  | h | long
INPUT_REGISTER | Read | 3286 |  | Chp / EC Power | Number of starts |  |  |  |  | long
INPUT_REGISTER | Read | 3288 |  | Chp / EC Power | Hours to Maintenance |  |  |  | h | int
INPUT_REGISTER | Read | 3290 |  | Chp | Output Power Setpoint |  |  |  | kW | int
INPUT_REGISTER | Read | 3291 |  | Chp | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 3296 |  | Chp | irBitblock |  |  |  |  | int
| Read |  | 0 | Chp | Warning |  |  |  |  | bit
| Read |  | 1 | Chp / EC Power | Malfunction |  |  |  |  | bit
| Read |  | 2 | Chp / EC Power | Controlled Shutdown |  |  |  |  | bit
| Read |  | 3 | Chp / EC Power | Generator On |  |  |  |  | bit
| Read |  | 4 | Chp | Automatic On |  |  |  |  | bit
| Read |  | 5 | Chp / EC Power | Automatic Ready |  |  |  |  | bit
| Read |  | 11 | Chp / EC Power | Output On Request |  |  |  |  | bit
INPUT_REGISTER | Read | 3304 |  | Water Treatment Module | Program Step |  |  | 20-140: Desalination not active 10000-10810: One time desalination 20000-20810: Automatic desalination 30000-30260: Stationary operation |  | int
INPUT_REGISTER | Read | 3305 |  | Water Treatment Module | Temperature Desalinization |  |  |  | °C | int | x10
INPUT_REGISTER | Read | 3306 |  | Water Treatment Module | Volume Flow |  |  |  | L/min | int | x10
INPUT_REGISTER | Read | 3307 |  | Water Treatment Module | Conductivity system |  |  |  | uS/cm | int | x10
INPUT_REGISTER | Read | 3308 |  | Water Treatment Module | Conductivity cartridge |  |  |  | uS/cm | int | x10
INPUT_REGISTER | Read | 3309 |  | Water Treatment Module | Cartridge Capacity |  |  |  | % | int
INPUT_REGISTER | Read | 3313 |  | Solar Data | Collector temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3314 |  | Solar Data | Temperature cylinder bottom |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3315 |  | Solar Data | Solar pump modulation setpoint |  |  |  | % | int
INPUT_REGISTER | Read | 3316 |  | Solar | Solar pump status | 0 | 19 | 1-TestMod 2-BlckProt 3-No heat 4-Ht avail 5-SolOff 6-MaxCyl 7-MaxColl 8-MinColl 9-FrostP 10-VacFct 11-SwChck 12-MixPrio 13-Switch 14-Priority 15-ThermD 16-MixCal 17-MixOpn 18-MixCl 19-MixOff |  | int
INPUT_REGISTER | Read | 3317 |  | Solar Data | Heat exchanger temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3318 |  | Solar Data | Heat exchanger pump modulation setpoint |  |  |  | % | int
INPUT_REGISTER | Read | 3319 |  | Solar | Heat exchanger pump status | 0 | 19 | 1-TestMod 2-BlckProt 3-No heat 4-Ht avail 5-SolOff 6-MaxCyl 7-MaxColl 8-MinColl 9-FrostP 10-VacFct 11-SwChck 12-MixPrio 13-Switch 14-Priority 15-ThermD 16-MixCal 17-MixOpn 18-MixCl 19-MixOff |  | int
INPUT_REGISTER | Read | 3320 |  | Solar Data | Temperature cylinder 3 top |  |  |  | °C | int | x10
INPUT_REGISTER | Read | 3321 |  | Solar Data | Reload pump modulation setpoint |  |  |  | % | int
INPUT_REGISTER | Read | 3322 |  | Solar | Reload pump status | 0 | 19 | 1-TestMod 2-BlckProt 3-No heat 4-Ht avail 5-SolOff 6-MaxCyl 7-MaxColl 8-MinColl 9-FrostP 10-VacFct 11-SwChck 12-MixPrio 13-Switch 14-Priority 15-ThermD 16-MixCal 17-MixOpn 18-MixCl 19-MixOff |  | int
INPUT_REGISTER | Read | 3323 |  | Solar | Pump therm. disinfect. status | 0 | 19 | 1-TestMod 2-BlckProt 3-No heat 4-Ht avail 5-SolOff 6-MaxCyl 7-MaxColl 8-MinColl 9-FrostP 10-VacFct 11-SwChck 12-MixPrio 13-Switch 14-Priority 15-ThermD 16-MixCal 17-MixOpn 18-MixCl 19-MixOff |  | int
INPUT_REGISTER | Read | 3324 |  | Solar Yield | Flow temperature heat meter |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3325 |  | Solar Yield | Return temperature heat meter |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3326 |  | Solar Yield | Heat count pulse counter | 0 | 15 |  |  | int
INPUT_REGISTER | Read | 3327 |  | Solar Yield | Solar yield per month |  |  |  | kWh | long | x10
INPUT_REGISTER | Read | 3329 |  | Solar Yield | Solar yield per year |  |  |  | kWh | long | x10
INPUT_REGISTER | Read | 3331 |  | Solar Yield | Last hour solar yield |  |  |  | kWh | long | x10
INPUT_REGISTER | Read | 3333 |  | Solar Yield | Solar yield per day |  |  |  | kWh | long | x10
INPUT_REGISTER | Read | 3335 |  | Solar Yield | Solar yield since installation |  |  |  | kWh | long | x10
INPUT_REGISTER | Read | 3337 |  | Solar | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 3338 |  | Solar Data | Hydraulic configuration |  |  |  |  | int
| Read |  | 0 | Solar | Option 1 active |  |  |  |  | bit
| Read |  | 1 | Solar | Option A active |  |  |  |  | bit
| Read |  | 2 | Solar | Option B active |  |  |  |  | bit
| Read |  | 3 | Solar | Option C active |  |  |  |  | bit
| Read |  | 4 | Solar | Option D active |  |  |  |  | bit
| Read |  | 5 | Solar | Option E active |  |  |  |  | bit
| Read |  | 6 | Solar | Option F active |  |  |  |  | bit
| Read |  | 7 | Solar | Option G active |  |  |  |  | bit
| Read |  | 8 | Solar | Option H active |  |  |  |  | bit
| Read |  | 9 | Solar | Option I active |  |  |  |  | bit
| Read |  | 10 | Solar | Option J active |  |  |  |  | bit
| Read |  | 11 | Solar | Option K active |  |  |  |  | bit
| Read |  | 12 | Solar | Option L active |  |  |  |  | bit
| Read |  | 13 | Solar | Option M active |  |  |  |  | bit
| Read |  | 14 | Solar | Option N active |  |  |  |  | bit
| Read |  | 15 | Solar | Option P active |  |  |  |  | bit
INPUT_REGISTER | Read | 3339 |  | Solar Data | irBitblock |  |  |  |  | int
| Read |  | 0 | Solar | Is Active |  |  |  |  | bit
INPUT_REGISTER |  | 3400 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 3401 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 3402 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 3403 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 3404 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 3405 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 3406 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 3407 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 3408 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 3409 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 3410 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 3411 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 3412 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 3413 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER | Read | 3422 |  | Energy Monitoring | Heat Output |  |  |  | kW | signed int | x10
INPUT_REGISTER | Read | 3423 |  | Energy Monitoring | Gas Consumption (LCV) |  |  |  | kW | signed int | x10
INPUT_REGISTER | Read | 3425 |  | Energy Monitoring | Electrical Power |  |  |  | W | int
INPUT_REGISTER | Read | 3430 |  | Fresh Water Characteristics 1 | DHW Out Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3431 |  | Fresh Water Characteristics 1 | DHW Volume Flow |  |  |  | L/min | signed int | x10
INPUT_REGISTER | Read | 3432 |  | Fresh Water Characteristics 1 | Prim In Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3433 |  | Fresh Water Characteristics 1 | DHW In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3434 |  | Fresh Water Characteristics 1 | Primary Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 3435 |  | Fresh Water Characteristics 1 | Request DHW Out Temperature |  |  |  | °C | int
INPUT_REGISTER | Read | 3436 |  | Fresh Water Characteristics 1 | Status Request DHW Out Temperature | 0 | 9 | 0-Off 1-DHWRed 2-DHW 3-Sol_red 4-Once_on 5-Therm_d 6-DlyHtUp 7-Preheat_start 8-Preheat_normal 9-No_eq |  | int
INPUT_REGISTER | Read | 3437 |  | Fresh Water Characteristics 2 | Circulation Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 3438 |  | Fresh Water Characteristics 2 | Status Circulation Pump | 0 | 8 | 0-Undefined 1-Test 2-BlckProt 3-No_req 4-AutoOff 5-AutoOn 6-Therm_d 7-Sys_Off 8-DlyHtUp |  | int
INPUT_REGISTER | Read | 3439 |  | Fresh Water Characteristics 2 | Return Valve Modulation Request |  |  |  | % | int
INPUT_REGISTER | Read | 3440 |  | Fresh Water Characteristics 2 | Valve State | 0 | 5 | 0-Undefined 1-TestMod 2-BlckProt 3-Mix_cl 4-Mix_opn 5-Sys_Off |  | int
INPUT_REGISTER | Read | 3441 |  | Fresh Water Characteristics 2 | Return Valve Buffer Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3442 |  | Fresh Water Characteristics 2 | Disinfection Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 3443 |  | Fresh Water Characteristics 2 | Pump State | 0 | 5 | 0-Undefined 1-TestMod 2-BlckPro 3-No_eq 4-Ht_req 5-Sys_Off |  | int
INPUT_REGISTER | Read | 3444 |  | Fresh Water Characteristics 1 | DHW Valve Power |  |  |  | % | int
INPUT_REGISTER | Read | 3445 |  | Fresh Water Characteristics 2 | Total Flow |  |  |  | L/min | int | x10
INPUT_REGISTER | Read | 3446 |  | Fresh Water 2 | Module 2 DHW Out Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3447 |  | Fresh Water 2 | Module 2 DHW Volume Flow |  |  |  | L/min | signed int | x10
INPUT_REGISTER | Read | 3448 |  | Fresh Water 2 | Module 2 Prim In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3449 |  | Fresh Water 2 | Module 2 DHW In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3450 |  | Fresh Water 2 | Module 2 DHW Valve Power |  |  |  | % | int
INPUT_REGISTER | Read | 3451 |  | Fresh Water 2 | Module 2 Prim Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 3452 |  | Fresh Water 2 | Module 2 Status Prim Pump |  |  |  |  | int
INPUT_REGISTER | Read | 3453 |  | Fresh Water 3 | Module 3 DHW Out Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3454 |  | Fresh Water 3 | Module 3 DHW Volume Flow |  |  |  | L/min | signed int | x10
INPUT_REGISTER | Read | 3455 |  | Fresh Water 3 | Module 3 Prim In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3456 |  | Fresh Water 3 | Module 3 DHW In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3457 |  | Fresh Water 3 | Module 3 DHW Valve Power |  |  |  | % | int
INPUT_REGISTER | Read | 3458 |  | Fresh Water 3 | Module 3 Prim Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 3459 |  | Fresh Water 3 | Module 3 Status Prim Pump |  |  |  |  | int
INPUT_REGISTER | Read | 3460 |  | Fresh Water 4 | Module 4 DHW Out Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3461 |  | Fresh Water 4 | Module 4 DHW Volume Flow |  |  |  | L/min | signed int | x10
INPUT_REGISTER | Read | 3462 |  | Fresh Water 4 | Module 4 Prim In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3463 |  | Fresh Water 4 | Module 4 DHW In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3464 |  | Fresh Water 4 | Module 4 DHW ValvePower |  |  |  | % | int
INPUT_REGISTER | Read | 3465 |  | Fresh Water 4 | Module 4 Prim Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 3466 |  | Fresh Water 4 | Module 4 Status Primary Pump |  |  |  |  | int
INPUT_REGISTER | Read | 3467 |  | Fresh Water | Fresh Water Hmi State |  |  |  |  | int
INPUT_REGISTER | Read | 3468 |  | Fresh Water Characteristics 3 | Fresh Water Configurations |  |  |  |  | int
| Read |  | 0 | Fresh Water | Option 2 active |  |  |  |  | bit
| Read |  | 1 | Fresh Water | Option A active |  |  |  |  | bit
| Read |  | 2 | Fresh Water | Option B active |  |  |  |  | bit
| Read |  | 3 | Fresh Water | Option C active |  |  |  |  | bit
| Read |  | 4 | Fresh Water | Option D active |  |  |  |  | bit
| Read |  | 5 | Fresh Water | Option E active |  |  |  |  | bit
| Read |  | 6 | Fresh Water | Option E active cascade module 2 active |  |  |  |  | bit
| Read |  | 7 | Fresh Water | Option E active cascade module 3 active |  |  |  |  | bit
| Read |  | 8 | Fresh Water | Option E active cascade module 4 active |  |  |  |  | bit
| Read |  | 9 | Fresh Water | Is Active |  |  |  |  | bit
INPUT_REGISTER | Read | 3476 |  | System | Error Key 1 |  |  |  |  | long
INPUT_REGISTER | Read | 3478 |  | System | Error Key 2 |  |  |  |  | long
INPUT_REGISTER | Read | 3480 |  | System | Error Key 3 |  |  |  |  | long
INPUT_REGISTER | Read | 3482 |  | System | Error Key 4 |  |  |  |  | long
INPUT_REGISTER | Read | 3484 |  | System | Error 1 Extra Info (MSB) |  |  |  |  | long
INPUT_REGISTER | Read | 3486 |  | System | Error 1 Extra Info (LSB) |  |  |  |  | long
INPUT_REGISTER | Read | 3488 |  | System | Error 2 Extra Info (MSB) |  |  |  |  | long
INPUT_REGISTER | Read | 3490 |  | System | Error 2 Extra Info (LSB) |  |  |  |  | long
INPUT_REGISTER | Read | 3492 |  | System | Error 3 Extra Info (MSB) |  |  |  |  | long
INPUT_REGISTER | Read | 3494 |  | System | Error 3 Extra Info (LSB) |  |  |  |  | long
INPUT_REGISTER | Read | 3496 |  | System | Error 4 Extra Info (MSB) |  |  |  |  | long
INPUT_REGISTER | Read | 3498 |  | System | Error 4 Extra Info (LSB) |  |  |  |  | long

## Slave07
Register Type | Permissions | Address | Bitblock Bit | Component | Name | Min | Max | Range | Unit | DataType | Float to Int Factor
HOLDING_REGISTER | Write | 3507 |  | DomesticHotWater Zm/Ems | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 3508 |  | DomesticHotWater Zm/Ems | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 3509 |  | DomesticHotWater Zm/Ems | Thermal Disinfection Setpoint | 65 | 75 |  | °C | int | x10
HOLDING_REGISTER | Write | 3510 |  | DomesticHotWater Zm | Setpoint Auto Day | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 3511 |  | DomesticHotWater Zm | Setpoint Auto Night | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 3512 |  | DomesticHotWater Zm | Setpoint Manual Day | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 3513 |  | DomesticHotWater Zm | Setpoint Manual Night | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 3514 |  | DomesticHotWater Zm | Setpoint Holiday | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 3515 |  | DomesticHotWater Zm/Ems | Circulation Pump Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 3516 |  | DomesticHotWater Zm/Ems | Circulation Pump Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 3517 |  | DomesticHotWater Zm/Ems | Disinfection Frequency | 0 | 7 | 0-Daily 1-Monday 2-Tuesday 3-Wednesday 4-Thursday 5-Friday 6-Saturday 7-Sunday |  | int
HOLDING_REGISTER | Write | 3518 |  | DomesticHotWater Zm/Ems | Disinfection Start Hour | 0 | 23 |  | h | int
HOLDING_REGISTER | Write | 3521 |  | DomesticHotWater Fm | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 3522 |  | DomesticHotWater Fm | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 3523 |  | DomesticHotWater Fm | Thermal Disinfection Setpoint | 65 | 75 |  | °C | int | x10
HOLDING_REGISTER | Write | 3524 |  | DomesticHotWater Fm | Setpoint Auto Day | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 3525 |  | DomesticHotWater Fm | Setpoint Auto Night | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 3526 |  | DomesticHotWater Fm | Setpoint Manual Day | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 3527 |  | DomesticHotWater Fm | Setpoint Manual Night | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 3528 |  | DomesticHotWater Fm | Setpoint Holiday | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 3529 |  | DomesticHotWater Fm | Circulation Pump Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 3530 |  | DomesticHotWater Fm | Circulation Pump Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 3531 |  | DomesticHotWater Fm | Disinfection Frequency | 0 | 7 | 0-Daily 1-Monday 2-Tuesday 3-Wednesday 4-Thursday 5-Friday 6-Saturday 7-Sunday |  | int
HOLDING_REGISTER | Write | 3532 |  | DomesticHotWater Fm | Disinfection Start Hour | 0 | 23 |  | h | int
HOLDING_REGISTER | Read | 3539 |  | Boiler | Control Type | 0 | 4 | 0-None 1-Safe 2-Ems 3-7Pole 4-Substation |  | int
HOLDING_REGISTER | Write | 3543 |  | AlternativeHeatSource | Operation Mode Request Auto Day | 20 | 99 |  | °C | int
HOLDING_REGISTER | Write | 3544 |  | AlternativeHeatSource | Operation Mode Request Auto Night | 20 | 99 |  | °C | int
HOLDING_REGISTER | Write | 3545 |  | AlternativeHeatSource | Operation Mode Request Manual Day | 20 | 99 |  | °C | int
HOLDING_REGISTER | Write | 3546 |  | AlternativeHeatSource | Operation Mode Request Manual Night | 20 | 99 |  | °C | int
HOLDING_REGISTER | Write | 3547 |  | AlternativeHeatSource | Operation Mode Request Holiday | 20 | 99 |  | °C | int
HOLDING_REGISTER | Write | 3548 |  | AlternativeHeatSource | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 3549 |  | AlternativeHeatSource | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 3550 |  | AlternativeHeatSource | Return Control Setpoint User | 10 | 70 |  | °C | int
HOLDING_REGISTER | Write | 3557 |  | HydraulicCircuit Zm | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 3558 |  | HydraulicCircuit Zm | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 3559 |  | HydraulicCircuit Zm | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3560 |  | HydraulicCircuit Zm | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3561 |  | HydraulicCircuit Zm | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3562 |  | HydraulicCircuit Zm | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3563 |  | HydraulicCircuit Zm | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3564 |  | HydraulicCircuit Zm | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 3570 |  | HydraulicCircuit 1 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 3571 |  | HydraulicCircuit 1 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 3572 |  | HydraulicCircuit 1 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3573 |  | HydraulicCircuit 1 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3574 |  | HydraulicCircuit 1 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3575 |  | HydraulicCircuit 1 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3576 |  | HydraulicCircuit 1 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3577 |  | HydraulicCircuit 1 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 3583 |  | HydraulicCircuit 2 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 3584 |  | HydraulicCircuit 2 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 3585 |  | HydraulicCircuit 2 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3586 |  | HydraulicCircuit 2 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3587 |  | HydraulicCircuit 2 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3588 |  | HydraulicCircuit 2 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3589 |  | HydraulicCircuit 2 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3590 |  | HydraulicCircuit 2 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 3596 |  | HydraulicCircuit 3 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 3597 |  | HydraulicCircuit 3 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 3598 |  | HydraulicCircuit 3 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3599 |  | HydraulicCircuit 3 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3600 |  | HydraulicCircuit 3 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3601 |  | HydraulicCircuit 3 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3602 |  | HydraulicCircuit 3 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3603 |  | HydraulicCircuit 3 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 3609 |  | HydraulicCircuit 4 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 3610 |  | HydraulicCircuit 4 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 3611 |  | HydraulicCircuit 4 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3612 |  | HydraulicCircuit 4 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3613 |  | HydraulicCircuit 4 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3614 |  | HydraulicCircuit 4 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3615 |  | HydraulicCircuit 4 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3616 |  | HydraulicCircuit 4 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 3622 |  | HydraulicCircuit 5 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 3623 |  | HydraulicCircuit 5 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 3624 |  | HydraulicCircuit 5 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3625 |  | HydraulicCircuit 5 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3626 |  | HydraulicCircuit 5 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3627 |  | HydraulicCircuit 5 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3628 |  | HydraulicCircuit 5 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3629 |  | HydraulicCircuit 5 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 3635 |  | HydraulicCircuit 6 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 3636 |  | HydraulicCircuit 6 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 3637 |  | HydraulicCircuit 6 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3638 |  | HydraulicCircuit 6 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3639 |  | HydraulicCircuit 6 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3640 |  | HydraulicCircuit 6 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3641 |  | HydraulicCircuit 6 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3642 |  | HydraulicCircuit 6 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 3648 |  | HydraulicCircuit 7 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 3649 |  | HydraulicCircuit 7 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 3650 |  | HydraulicCircuit 7 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3651 |  | HydraulicCircuit 7 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3652 |  | HydraulicCircuit 7 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3653 |  | HydraulicCircuit 7 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3654 |  | HydraulicCircuit 7 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3655 |  | HydraulicCircuit 7 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 3661 |  | HydraulicCircuit 8 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 3662 |  | HydraulicCircuit 8 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 3663 |  | HydraulicCircuit 8 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3664 |  | HydraulicCircuit 8 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3665 |  | HydraulicCircuit 8 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3666 |  | HydraulicCircuit 8 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3667 |  | HydraulicCircuit 8 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 3668 |  | HydraulicCircuit 8 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 3701 |  | Heat Pump | Heat demand source | 0 | 2 | 0-Scheduler 1-System 2-Max_system_scheduler |  | int
HOLDING_REGISTER | Read | 3921 |  | Fresh Water Characteristics 3 | DHU Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 3922 |  | Fresh Water Characteristics 3 | Extra Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 3923 |  | Fresh Water Characteristics 3 | Maximum DHW Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 3924 |  | Fresh Water Characteristics 3 | On High Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 3925 |  | Fresh Water Characteristics 3 | On Low Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 3926 |  | Fresh Water Characteristics 3 | Fresh Water Type | 0 | 3 | 0-15/20l/min 1-27l/min 2-40l/min 3-60l/min |  | int
HOLDING_REGISTER | Read | 3927 |  | Fresh Water Characteristics 3 | Enable Alarm Output | 0 | 2 | 0-No 1-Yes 2-Inverted |  | int
HOLDING_REGISTER | Read | 3928 |  | Fresh Water Characteristics 3 | Buffer Cylinder Temperature Offset |  |  |  | K | int
HOLDING_REGISTER | Read | 3929 |  | Fresh Water Characteristics 3 | hrBitblock |  |  |  |  | int
| Read |  | 0 | Fresh Water | Buffer Cylinder Temperature Optimization Enabled |  |  |  |  | bit
| Read |  | 1 | Fresh Water | Impulse Enabled |  |  |  |  | bit
| Read |  | 2 | Fresh Water | Time Program Enabled |  |  |  |  | bit
HOLDING_REGISTER | Read | 3930 |  | Fresh Water Characteristics 3 | Minimum Buffer Cylinder Temperature Offset |  |  |  | K | int
HOLDING_REGISTER | Read | 3931 |  | Fresh Water Characteristics 2 | Circulation Pump Runs per Hour | 0 | 7 | 0-Undefined 1-1x3_minutes/h 2-2x3_minutes/h 3-3x3_minutes/h 4-4x3_minutes/h 5-5x3_minutes/h 6-6x3_minutes/h 7-Permanent |  | int
HOLDING_REGISTER | Read | 3932 |  | Fresh Water Characteristics 2 | Swich Hysteresis |  |  |  | K | int
HOLDING_REGISTER | Read | 3933 |  | Fresh Water Characteristics 2 | Thermal Disinfection Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 3934 |  | Fresh Water Characteristics 2 | Pre Heat Maximum Temperature |  |  |  | °C | int
INPUT_REGISTER | Read | 3500 |  | System | Own Outdoor temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3501 |  | System | Damped Own outdoor temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3504 |  | System | Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3508 |  | System | Active Functions 1 |  |  |  |  | int
INPUT_REGISTER | Read | 3509 |  | System | Active Functions 2 |  |  |  |  | int
INPUT_REGISTER | Read | 3515 |  | DomesticHotWater Zm | Charge Pump Running | 0 | 4 | 0-Stopping 1-Starting 2-Running 3-Off 4-Error |  | int
INPUT_REGISTER | Read | 3516 |  | DomesticHotWater Zm | Circulation Pump Running | 0 | 4 | 0-Stopping 1-Starting 2-Running 3-Off 4-Error |  | int
INPUT_REGISTER | Read | 3517 |  | DomesticHotWater Zm | Hydraulic State | 0 | 7 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Cold_load 6-Post_purge 7-Condense_protection |  | int
INPUT_REGISTER | Read | 3518 |  | DomesticHotWater Zm/Ems | Thermal Disinfection Status | 0 | 3 | 0-Off 1-On 2-Success 3-Error |  | int
INPUT_REGISTER | Read | 3519 |  | DomesticHotWater Zm/Ems | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 3520 |  | DomesticHotWater Zm/Ems | Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3521 |  | DomesticHotWater Zm/Ems | Current Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3531 |  | DomesticHotWater Fm | Charge Pump Running | 0 | 4 | 0-Stopping 1-Starting 2-Running 3-Off 4-Error |  | int
INPUT_REGISTER | Read | 3532 |  | DomesticHotWater Fm | Circulation Pump Running | 0 | 4 | 0-Stopping 1-Starting 2-Running 3-Off 4-Error |  | int
INPUT_REGISTER | Read | 3533 |  | DomesticHotWater Fm | Hydraulic State | 0 | 7 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Cold_load 6-Post_purge 7-Condense_protection |  | int
INPUT_REGISTER | Read | 3534 |  | DomesticHotWater Fm | Thermal Disinfection Status | 0 | 3 | 0-Off 1-On 2-Success 3-Error |  | int
INPUT_REGISTER | Read | 3535 |  | DomesticHotWater Fm | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 3536 |  | DomesticHotWater Fm | Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3537 |  | DomesticHotWater Fm | Current Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER |  | 3547 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 3548 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 3550 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 3552 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 3553 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 3554 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 3555 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 3556 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 3559 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 3560 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER | Read | 3563 |  | AlternativeHeatSource | Operating hours |  |  |  | h | long
INPUT_REGISTER | Read | 3565 |  | AlternativeHeatSource | Heat Source Starts |  |  |  |  | long
INPUT_REGISTER | Read | 3567 |  | AlternativeHeatSource | Heat Source Hours to Maintenance |  |  |  | h | int
INPUT_REGISTER | Read | 3569 |  | AlternativeHeatSource | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
| Read |  | 0 | AlternativeHeatSource | Is Heat Source On |  |  |  |  | bit
| Read |  | 1 | AlternativeHeatSource | Is Heat Source On Request |  |  |  |  | bit
INPUT_REGISTER | Read | 3587 |  | HydraulicCircuit Zm | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3588 |  | HydraulicCircuit Zm | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3589 |  | HydraulicCircuit Zm | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3590 |  | HydraulicCircuit Zm | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3591 |  | HydraulicCircuit Zm | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 3592 |  | HydraulicCircuit Zm | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 3593 |  | HydraulicCircuit Zm | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 3594 |  | HydraulicCircuit Zm | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 3595 |  | HydraulicCircuit Zm | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 3599 |  | HydraulicCircuit 1 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3600 |  | HydraulicCircuit 1 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3601 |  | HydraulicCircuit 1 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3602 |  | HydraulicCircuit 1 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3603 |  | HydraulicCircuit 1 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 3604 |  | HydraulicCircuit 1 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 3605 |  | HydraulicCircuit 1 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 3606 |  | HydraulicCircuit 1 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 3607 |  | HydraulicCircuit 1 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 3612 |  | HydraulicCircuit 2 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3613 |  | HydraulicCircuit 2 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3614 |  | HydraulicCircuit 2 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3615 |  | HydraulicCircuit 2 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3616 |  | HydraulicCircuit 2 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 3617 |  | HydraulicCircuit 2 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 3618 |  | HydraulicCircuit 2 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 3619 |  | HydraulicCircuit 2 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 3620 |  | HydraulicCircuit 2 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 3625 |  | HydraulicCircuit 3 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3626 |  | HydraulicCircuit 3 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3627 |  | HydraulicCircuit 3 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3628 |  | HydraulicCircuit 3 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3629 |  | HydraulicCircuit 3 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 3630 |  | HydraulicCircuit 3 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 3631 |  | HydraulicCircuit 3 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 3632 |  | HydraulicCircuit 3 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 3633 |  | HydraulicCircuit 3 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 3638 |  | HydraulicCircuit 4 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3639 |  | HydraulicCircuit 4 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3640 |  | HydraulicCircuit 4 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3641 |  | HydraulicCircuit 4 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3642 |  | HydraulicCircuit 4 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 3643 |  | HydraulicCircuit 4 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 3644 |  | HydraulicCircuit 4 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 3645 |  | HydraulicCircuit 4 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 3646 |  | HydraulicCircuit 4 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 3651 |  | HydraulicCircuit 5 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3652 |  | HydraulicCircuit 5 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3653 |  | HydraulicCircuit 5 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3654 |  | HydraulicCircuit 5 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3655 |  | HydraulicCircuit 5 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 3656 |  | HydraulicCircuit 5 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 3657 |  | HydraulicCircuit 5 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 3658 |  | HydraulicCircuit 5 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 3659 |  | HydraulicCircuit 5 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 3664 |  | HydraulicCircuit 6 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3665 |  | HydraulicCircuit 6 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3666 |  | HydraulicCircuit 6 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3667 |  | HydraulicCircuit 6 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3668 |  | HydraulicCircuit 6 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 3669 |  | HydraulicCircuit 6 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 3670 |  | HydraulicCircuit 6 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 3671 |  | HydraulicCircuit 6 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 3672 |  | HydraulicCircuit 6 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 3677 |  | HydraulicCircuit 7 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3678 |  | HydraulicCircuit 7 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3679 |  | HydraulicCircuit 7 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3680 |  | HydraulicCircuit 7 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3681 |  | HydraulicCircuit 7 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 3682 |  | HydraulicCircuit 7 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 3683 |  | HydraulicCircuit 7 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 3684 |  | HydraulicCircuit 7 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 3685 |  | HydraulicCircuit 7 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 3690 |  | HydraulicCircuit 8 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3691 |  | HydraulicCircuit 8 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3692 |  | HydraulicCircuit 8 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3693 |  | HydraulicCircuit 8 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3694 |  | HydraulicCircuit 8 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 3695 |  | HydraulicCircuit 8 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 3696 |  | HydraulicCircuit 8 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 3697 |  | HydraulicCircuit 8 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 3698 |  | HydraulicCircuit 8 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 3703 |  | i2c | Global Error State | 0 | 4 | 0-No_Error 1-i2c_driver_error 2-Wrong_Cycle_Time 3-Missing_Module_Slot 4-Module_Slot_Error |  | int
INPUT_REGISTER | Read | 3704 |  | i2c | Slot1 Module Detected |  |  | 0-Unknown 1-None 22-FM_CM 25-FM_SI 28-FM_MM 29-FM_MW 30-FM_AM 31-FM_CM2 |  | int
INPUT_REGISTER | Read | 3705 |  | i2c | Slot1 Error State |  |  | 0-No_Error 1-No_Response 2-Wrong_Module 3-Unsupported_Module 4-Internal_Sw_Error 5-Communication_Failed 6-Internal_Module_Error 7-Module_Not_Supported_Current_Variant 8-Module_Not_Suppported_In_Slot 9-Module_Count_Too_High 10-Module_Not_Supported_With_Connected_Boiler_Type |  | int
INPUT_REGISTER | Read | 3706 |  | i2c | Slot2 Module Detected |  |  | 0-Unknown 1-None 22-FM_CM 25-FM_SI 28-FM_MM 29-FM_MW 30-FM_AM 31-FM_CM2 |  | int
INPUT_REGISTER | Read | 3707 |  | i2c | Slot2 Error State |  |  | 0-No_Error 1-No_Response 2-Wrong_Module 3-Unsupported_Module 4-Internal_Sw_Error 5-Communication_Failed 6-Internal_Module_Error 7-Module_Not_Supported_Current_Variant 8-Module_Not_Suppported_In_Slot 9-Module_Count_Too_High 10-Module_Not_Supported_With_Connected_Boiler_Type |  | int
INPUT_REGISTER | Read | 3708 |  | i2c | Slot3 Module Detected |  |  | 0-Unknown 1-None 22-FM_CM 25-FM_SI 28-FM_MM 29-FM_MW 30-FM_AM 31-FM_CM2 |  | int
INPUT_REGISTER | Read | 3709 |  | i2c | Slot3 Error State |  |  | 0-No_Error 1-No_Response 2-Wrong_Module 3-Unsupported_Module 4-Internal_Sw_Error 5-Communication_Failed 6-Internal_Module_Error 7-Module_Not_Supported_Current_Variant 8-Module_Not_Suppported_In_Slot 9-Module_Count_Too_High 10-Module_Not_Supported_With_Connected_Boiler_Type |  | int
INPUT_REGISTER | Read | 3710 |  | i2c | Slot4 Module Detected |  |  | 0-Unknown 1-None 22-FM_CM 25-FM_SI 28-FM_MM 29-FM_MW 30-FM_AM 31-FM_CM2 |  | int
INPUT_REGISTER | Read | 3711 |  | i2c | Slot4 Error State |  |  | 0-No_Error 1-No_Response 2-Wrong_Module 3-Unsupported_Module 4-Internal_Sw_Error 5-Communication_Failed 6-Internal_Module_Error 7-Module_Not_Supported_Current_Variant 8-Module_Not_Suppported_In_Slot 9-Module_Count_Too_High 10-Module_Not_Supported_With_Connected_Boiler_Type |  | int
INPUT_REGISTER | Read | 3712 |  | i2c | Slot A Module Detected |  |  | 0-Unknown 1-None 26-ZM5313 27-ZM5311 |  | int
INPUT_REGISTER | Read | 3713 |  | i2c | Slot A Error State |  |  | 0-No_Error 1-No_Response 2-Wrong_Module 3-Unsupported_Module 4-Internal_Sw_Error 5-Communication_Failed 6-Internal_Module_Error 7-Module_Not_Supported_Current_Variant 8-Module_Not_Suppported_In_Slot 9-Module_Count_Too_High 10-Module_Not_Supported_With_Connected_Boiler_Type |  | int
INPUT_REGISTER | Read | 3714 |  | i2c | irBitblock |  |  |  |  | int
| Read |  | 0 | i2c | Component Error |  |  |  |  | bit
INPUT_REGISTER | Read | 3725 |  | fm-si | irBitblock |  |  |  |  | int
| Read |  | 0 | fm-si | Input 1 Error |  |  |  |  | bit
| Read |  | 1 | fm-si | Input 2 Error |  |  |  |  | bit
| Read |  | 2 | fm-si | Input 3 Error |  |  |  |  | bit
| Read |  | 3 | fm-si | Input 4 Error |  |  |  |  | bit
| Read |  | 4 | fm-si | Input 5 Error |  |  |  |  | bit
INPUT_REGISTER | Read | 3732 |  | Sdc | Demand Mode (Low Priority) | 0 | 2 | 0-Off 1-Take_Heat 2-Give_Heat |  | int
INPUT_REGISTER | Read | 3733 |  | Sdc | Demand Flow Temp (Low Priority) |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3734 |  | Sdc | Demand Mode (High Priority) | 0 | 2 | 0-Off 1-Take_Heat 2-Give_Heat |  | int
INPUT_REGISTER | Read | 3735 |  | Sdc | Demand Flow Temp (High Priority) |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3739 |  | Heat Pump | System return temperature for HP heating buffer |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3740 |  | Heat Pump | Buffer mid temperature for HP heating buffer |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3741 |  | Heat Pump | Buffer top temperature for HP heating buffer |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3742 |  | Heat Pump | Buffer bottom temperature for HP heating buffer |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3743 |  | Heat Pump | Return temperature FWR |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3744 |  | Heat Pump | Flow temperature FWV |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3745 |  | Heat Pump | Flow temperature HP |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3746 |  | Heat Pump | Return temperature HP |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3747 |  | Heat Pump | HMI State of HP Component | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 3748 |  | Heat Pump | HP current heat output |  |  |  | kW | signed int | x10
INPUT_REGISTER | Read | 3749 |  | Heat Pump | HP current electrical power consumption | 0 | 10000 |  | kW | int | x10
INPUT_REGISTER | Read | 3750 |  | Heat Pump | HP Smart grid mode | 0 | 3 | 0-normal_charging_grid 1-low_charging_grid 2-high_charging_grid 3-free_charging_grid |  | int
INPUT_REGISTER | Read | 3751 |  | Heat Pump | Heat demand temperature set point |  |  |  | °C | int
INPUT_REGISTER | Read | 3752 |  | Heat Pump | heatPumpStatusIrBitblock | 0 |  |  |  | int
INPUT_REGISTER | Read | 3753 |  | Heat Pump | Ambient Temperature HP |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3754 |  | Heat Pump | HP silent mode | 0 | 3 | 0-standard_mode 1-silent_mode 2-super_silent_mode 3-night_mode |  | int
INPUT_REGISTER | Read | 3755 |  | Heat Pump | Heat Pump Heat Request Temperature |  |  |  | °C | int
INPUT_REGISTER | Read | 3756 |  | Heat Pump | heatPumpIrBitblock |  |  |  |  | int
INPUT_REGISTER | Read | 3765 |  | System | Open Notifications Count |  |  |  |  | int
INPUT_REGISTER | Read | 3766 |  | System | Error Key 5 |  |  |  |  | long
INPUT_REGISTER | Read | 3768 |  | System | Error Key 6 |  |  |  |  | long
INPUT_REGISTER | Read | 3770 |  | System | Error Key 7 |  |  |  |  | long
INPUT_REGISTER | Read | 3772 |  | System | Error Key 8 |  |  |  |  | long
INPUT_REGISTER | Read | 3774 |  | System | Error Key 9 |  |  |  |  | long
INPUT_REGISTER | Read | 3776 |  | System | Error Key 10 |  |  |  |  | long
INPUT_REGISTER | Read | 3778 |  | Chp / EC Power | Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3779 |  | Chp / EC Power | Return Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3780 |  | Chp | Flue Gas Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3781 |  | Chp | Motor Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3782 |  | Chp / EC Power | Current Generator Power |  |  |  | kW | int
INPUT_REGISTER | Read | 3783 |  | Chp | Current Power Setpoint |  |  |  | kW | int
INPUT_REGISTER | Read | 3784 |  | Chp / EC Power | Operation Hours |  |  |  | h | long
INPUT_REGISTER | Read | 3786 |  | Chp / EC Power | Number of starts |  |  |  |  | long
INPUT_REGISTER | Read | 3788 |  | Chp / EC Power | Hours to Maintenance |  |  |  | h | int
INPUT_REGISTER | Read | 3790 |  | Chp | Output Power Setpoint |  |  |  | kW | int
INPUT_REGISTER | Read | 3791 |  | Chp | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 3796 |  | Chp | irBitblock |  |  |  |  | int
| Read |  | 0 | Chp | Warning |  |  |  |  | bit
| Read |  | 1 | Chp / EC Power | Malfunction |  |  |  |  | bit
| Read |  | 2 | Chp / EC Power | Controlled Shutdown |  |  |  |  | bit
| Read |  | 3 | Chp / EC Power | Generator On |  |  |  |  | bit
| Read |  | 4 | Chp | Automatic On |  |  |  |  | bit
| Read |  | 5 | Chp / EC Power | Automatic Ready |  |  |  |  | bit
| Read |  | 11 | Chp / EC Power | Output On Request |  |  |  |  | bit
INPUT_REGISTER | Read | 3804 |  | Water Treatment Module | Program Step |  |  | 20-140: Desalination not active 10000-10810: One time desalination 20000-20810: Automatic desalination 30000-30260: Stationary operation |  | int
INPUT_REGISTER | Read | 3805 |  | Water Treatment Module | Temperature Desalinization |  |  |  | °C | int | x10
INPUT_REGISTER | Read | 3806 |  | Water Treatment Module | Volume Flow |  |  |  | L/min | int | x10
INPUT_REGISTER | Read | 3807 |  | Water Treatment Module | Conductivity system |  |  |  | uS/cm | int | x10
INPUT_REGISTER | Read | 3808 |  | Water Treatment Module | Conductivity cartridge |  |  |  | uS/cm | int | x10
INPUT_REGISTER | Read | 3809 |  | Water Treatment Module | Cartridge Capacity |  |  |  | % | int
INPUT_REGISTER | Read | 3813 |  | Solar Data | Collector temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3814 |  | Solar Data | Temperature cylinder bottom |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3815 |  | Solar Data | Solar pump modulation setpoint |  |  |  | % | int
INPUT_REGISTER | Read | 3816 |  | Solar | Solar pump status | 0 | 19 | 1-TestMod 2-BlckProt 3-No heat 4-Ht avail 5-SolOff 6-MaxCyl 7-MaxColl 8-MinColl 9-FrostP 10-VacFct 11-SwChck 12-MixPrio 13-Switch 14-Priority 15-ThermD 16-MixCal 17-MixOpn 18-MixCl 19-MixOff |  | int
INPUT_REGISTER | Read | 3817 |  | Solar Data | Heat exchanger temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3818 |  | Solar Data | Heat exchanger pump modulation setpoint |  |  |  | % | int
INPUT_REGISTER | Read | 3819 |  | Solar | Heat exchanger pump status | 0 | 19 | 1-TestMod 2-BlckProt 3-No heat 4-Ht avail 5-SolOff 6-MaxCyl 7-MaxColl 8-MinColl 9-FrostP 10-VacFct 11-SwChck 12-MixPrio 13-Switch 14-Priority 15-ThermD 16-MixCal 17-MixOpn 18-MixCl 19-MixOff |  | int
INPUT_REGISTER | Read | 3820 |  | Solar Data | Temperature cylinder 3 top |  |  |  | °C | int | x10
INPUT_REGISTER | Read | 3821 |  | Solar Data | Reload pump modulation setpoint |  |  |  | % | int
INPUT_REGISTER | Read | 3822 |  | Solar | Reload pump status | 0 | 19 | 1-TestMod 2-BlckProt 3-No heat 4-Ht avail 5-SolOff 6-MaxCyl 7-MaxColl 8-MinColl 9-FrostP 10-VacFct 11-SwChck 12-MixPrio 13-Switch 14-Priority 15-ThermD 16-MixCal 17-MixOpn 18-MixCl 19-MixOff |  | int
INPUT_REGISTER | Read | 3823 |  | Solar | Pump therm. disinfect. status | 0 | 19 | 1-TestMod 2-BlckProt 3-No heat 4-Ht avail 5-SolOff 6-MaxCyl 7-MaxColl 8-MinColl 9-FrostP 10-VacFct 11-SwChck 12-MixPrio 13-Switch 14-Priority 15-ThermD 16-MixCal 17-MixOpn 18-MixCl 19-MixOff |  | int
INPUT_REGISTER | Read | 3824 |  | Solar Yield | Flow temperature heat meter |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3825 |  | Solar Yield | Return temperature heat meter |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3826 |  | Solar Yield | Heat count pulse counter | 0 | 15 |  |  | int
INPUT_REGISTER | Read | 3827 |  | Solar Yield | Solar yield per month |  |  |  | kWh | long | x10
INPUT_REGISTER | Read | 3829 |  | Solar Yield | Solar yield per year |  |  |  | kWh | long | x10
INPUT_REGISTER | Read | 3831 |  | Solar Yield | Last hour solar yield |  |  |  | kWh | long | x10
INPUT_REGISTER | Read | 3833 |  | Solar Yield | Solar yield per day |  |  |  | kWh | long | x10
INPUT_REGISTER | Read | 3835 |  | Solar Yield | Solar yield since installation |  |  |  | kWh | long | x10
INPUT_REGISTER | Read | 3837 |  | Solar | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 3838 |  | Solar Data | Hydraulic configuration |  |  |  |  | int
| Read |  | 0 | Solar | Option 1 active |  |  |  |  | bit
| Read |  | 1 | Solar | Option A active |  |  |  |  | bit
| Read |  | 2 | Solar | Option B active |  |  |  |  | bit
| Read |  | 3 | Solar | Option C active |  |  |  |  | bit
| Read |  | 4 | Solar | Option D active |  |  |  |  | bit
| Read |  | 5 | Solar | Option E active |  |  |  |  | bit
| Read |  | 6 | Solar | Option F active |  |  |  |  | bit
| Read |  | 7 | Solar | Option G active |  |  |  |  | bit
| Read |  | 8 | Solar | Option H active |  |  |  |  | bit
| Read |  | 9 | Solar | Option I active |  |  |  |  | bit
| Read |  | 10 | Solar | Option J active |  |  |  |  | bit
| Read |  | 11 | Solar | Option K active |  |  |  |  | bit
| Read |  | 12 | Solar | Option L active |  |  |  |  | bit
| Read |  | 13 | Solar | Option M active |  |  |  |  | bit
| Read |  | 14 | Solar | Option N active |  |  |  |  | bit
| Read |  | 15 | Solar | Option P active |  |  |  |  | bit
INPUT_REGISTER | Read | 3839 |  | Solar Data | irBitblock |  |  |  |  | int
| Read |  | 0 | Solar | Is Active |  |  |  |  | bit
INPUT_REGISTER |  | 3900 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 3901 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 3902 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 3903 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 3904 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 3905 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 3906 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 3907 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 3908 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 3909 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 3910 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 3911 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 3912 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 3913 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER | Read | 3922 |  | Energy Monitoring | Heat Output |  |  |  | kW | signed int | x10
INPUT_REGISTER | Read | 3923 |  | Energy Monitoring | Gas Consumption (LCV) |  |  |  | kW | signed int | x10
INPUT_REGISTER | Read | 3925 |  | Energy Monitoring | Electrical Power |  |  |  | W | int
INPUT_REGISTER | Read | 3930 |  | Fresh Water Characteristics 1 | DHW Out Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3931 |  | Fresh Water Characteristics 1 | DHW Volume Flow |  |  |  | L/min | signed int | x10
INPUT_REGISTER | Read | 3932 |  | Fresh Water Characteristics 1 | Prim In Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3933 |  | Fresh Water Characteristics 1 | DHW In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3934 |  | Fresh Water Characteristics 1 | Primary Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 3935 |  | Fresh Water Characteristics 1 | Request DHW Out Temperature |  |  |  | °C | int
INPUT_REGISTER | Read | 3936 |  | Fresh Water Characteristics 1 | Status Request DHW Out Temperature | 0 | 9 | 0-Off 1-DHWRed 2-DHW 3-Sol_red 4-Once_on 5-Therm_d 6-DlyHtUp 7-Preheat_start 8-Preheat_normal 9-No_eq |  | int
INPUT_REGISTER | Read | 3937 |  | Fresh Water Characteristics 2 | Circulation Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 3938 |  | Fresh Water Characteristics 2 | Status Circulation Pump | 0 | 8 | 0-Undefined 1-Test 2-BlckProt 3-No_req 4-AutoOff 5-AutoOn 6-Therm_d 7-Sys_Off 8-DlyHtUp |  | int
INPUT_REGISTER | Read | 3939 |  | Fresh Water Characteristics 2 | Return Valve Modulation Request |  |  |  | % | int
INPUT_REGISTER | Read | 3940 |  | Fresh Water Characteristics 2 | Valve State | 0 | 5 | 0-Undefined 1-TestMod 2-BlckProt 3-Mix_cl 4-Mix_opn 5-Sys_Off |  | int
INPUT_REGISTER | Read | 3941 |  | Fresh Water Characteristics 2 | Return Valve Buffer Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3942 |  | Fresh Water Characteristics 2 | Disinfection Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 3943 |  | Fresh Water Characteristics 2 | Pump State | 0 | 5 | 0-Undefined 1-TestMod 2-BlckPro 3-No_eq 4-Ht_req 5-Sys_Off |  | int
INPUT_REGISTER | Read | 3944 |  | Fresh Water Characteristics 1 | DHW Valve Power |  |  |  | % | int
INPUT_REGISTER | Read | 3945 |  | Fresh Water Characteristics 2 | Total Flow |  |  |  | L/min | int | x10
INPUT_REGISTER | Read | 3946 |  | Fresh Water 2 | Module 2 DHW Out Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3947 |  | Fresh Water 2 | Module 2 DHW Volume Flow |  |  |  | L/min | signed int | x10
INPUT_REGISTER | Read | 3948 |  | Fresh Water 2 | Module 2 Prim In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3949 |  | Fresh Water 2 | Module 2 DHW In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3950 |  | Fresh Water 2 | Module 2 DHW Valve Power |  |  |  | % | int
INPUT_REGISTER | Read | 3951 |  | Fresh Water 2 | Module 2 Prim Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 3952 |  | Fresh Water 2 | Module 2 Status Prim Pump |  |  |  |  | int
INPUT_REGISTER | Read | 3953 |  | Fresh Water 3 | Module 3 DHW Out Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3954 |  | Fresh Water 3 | Module 3 DHW Volume Flow |  |  |  | L/min | signed int | x10
INPUT_REGISTER | Read | 3955 |  | Fresh Water 3 | Module 3 Prim In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3956 |  | Fresh Water 3 | Module 3 DHW In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3957 |  | Fresh Water 3 | Module 3 DHW Valve Power |  |  |  | % | int
INPUT_REGISTER | Read | 3958 |  | Fresh Water 3 | Module 3 Prim Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 3959 |  | Fresh Water 3 | Module 3 Status Prim Pump |  |  |  |  | int
INPUT_REGISTER | Read | 3960 |  | Fresh Water 4 | Module 4 DHW Out Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3961 |  | Fresh Water 4 | Module 4 DHW Volume Flow |  |  |  | L/min | signed int | x10
INPUT_REGISTER | Read | 3962 |  | Fresh Water 4 | Module 4 Prim In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3963 |  | Fresh Water 4 | Module 4 DHW In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 3964 |  | Fresh Water 4 | Module 4 DHW ValvePower |  |  |  | % | int
INPUT_REGISTER | Read | 3965 |  | Fresh Water 4 | Module 4 Prim Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 3966 |  | Fresh Water 4 | Module 4 Status Primary Pump |  |  |  |  | int
INPUT_REGISTER | Read | 3967 |  | Fresh Water | Fresh Water Hmi State |  |  |  |  | int
INPUT_REGISTER | Read | 3968 |  | Fresh Water Characteristics 3 | Fresh Water Configurations |  |  |  |  | int
| Read |  | 0 | Fresh Water | Option 2 active |  |  |  |  | bit
| Read |  | 1 | Fresh Water | Option A active |  |  |  |  | bit
| Read |  | 2 | Fresh Water | Option B active |  |  |  |  | bit
| Read |  | 3 | Fresh Water | Option C active |  |  |  |  | bit
| Read |  | 4 | Fresh Water | Option D active |  |  |  |  | bit
| Read |  | 5 | Fresh Water | Option E active |  |  |  |  | bit
| Read |  | 6 | Fresh Water | Option E active cascade module 2 active |  |  |  |  | bit
| Read |  | 7 | Fresh Water | Option E active cascade module 3 active |  |  |  |  | bit
| Read |  | 8 | Fresh Water | Option E active cascade module 4 active |  |  |  |  | bit
| Read |  | 9 | Fresh Water | Is Active |  |  |  |  | bit
INPUT_REGISTER | Read | 3976 |  | System | Error Key 1 |  |  |  |  | long
INPUT_REGISTER | Read | 3978 |  | System | Error Key 2 |  |  |  |  | long
INPUT_REGISTER | Read | 3980 |  | System | Error Key 3 |  |  |  |  | long
INPUT_REGISTER | Read | 3982 |  | System | Error Key 4 |  |  |  |  | long
INPUT_REGISTER | Read | 3984 |  | System | Error 1 Extra Info (MSB) |  |  |  |  | long
INPUT_REGISTER | Read | 3986 |  | System | Error 1 Extra Info (LSB) |  |  |  |  | long
INPUT_REGISTER | Read | 3988 |  | System | Error 2 Extra Info (MSB) |  |  |  |  | long
INPUT_REGISTER | Read | 3990 |  | System | Error 2 Extra Info (LSB) |  |  |  |  | long
INPUT_REGISTER | Read | 3992 |  | System | Error 3 Extra Info (MSB) |  |  |  |  | long
INPUT_REGISTER | Read | 3994 |  | System | Error 3 Extra Info (LSB) |  |  |  |  | long
INPUT_REGISTER | Read | 3996 |  | System | Error 4 Extra Info (MSB) |  |  |  |  | long
INPUT_REGISTER | Read | 3998 |  | System | Error 4 Extra Info (LSB) |  |  |  |  | long

## Slave08
Register Type | Permissions | Address | Bitblock Bit | Component | Name | Min | Max | Range | Unit | DataType | Float to Int Factor
HOLDING_REGISTER | Write | 4007 |  | DomesticHotWater Zm/Ems | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 4008 |  | DomesticHotWater Zm/Ems | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 4009 |  | DomesticHotWater Zm/Ems | Thermal Disinfection Setpoint | 65 | 75 |  | °C | int | x10
HOLDING_REGISTER | Write | 4010 |  | DomesticHotWater Zm | Setpoint Auto Day | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 4011 |  | DomesticHotWater Zm | Setpoint Auto Night | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 4012 |  | DomesticHotWater Zm | Setpoint Manual Day | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 4013 |  | DomesticHotWater Zm | Setpoint Manual Night | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 4014 |  | DomesticHotWater Zm | Setpoint Holiday | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 4015 |  | DomesticHotWater Zm/Ems | Circulation Pump Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 4016 |  | DomesticHotWater Zm/Ems | Circulation Pump Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 4017 |  | DomesticHotWater Zm/Ems | Disinfection Frequency | 0 | 7 | 0-Daily 1-Monday 2-Tuesday 3-Wednesday 4-Thursday 5-Friday 6-Saturday 7-Sunday |  | int
HOLDING_REGISTER | Write | 4018 |  | DomesticHotWater Zm/Ems | Disinfection Start Hour | 0 | 23 |  | h | int
HOLDING_REGISTER | Write | 4021 |  | DomesticHotWater Fm | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 4022 |  | DomesticHotWater Fm | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 4023 |  | DomesticHotWater Fm | Thermal Disinfection Setpoint | 65 | 75 |  | °C | int | x10
HOLDING_REGISTER | Write | 4024 |  | DomesticHotWater Fm | Setpoint Auto Day | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 4025 |  | DomesticHotWater Fm | Setpoint Auto Night | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 4026 |  | DomesticHotWater Fm | Setpoint Manual Day | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 4027 |  | DomesticHotWater Fm | Setpoint Manual Night | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 4028 |  | DomesticHotWater Fm | Setpoint Holiday | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 4029 |  | DomesticHotWater Fm | Circulation Pump Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 4030 |  | DomesticHotWater Fm | Circulation Pump Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 4031 |  | DomesticHotWater Fm | Disinfection Frequency | 0 | 7 | 0-Daily 1-Monday 2-Tuesday 3-Wednesday 4-Thursday 5-Friday 6-Saturday 7-Sunday |  | int
HOLDING_REGISTER | Write | 4032 |  | DomesticHotWater Fm | Disinfection Start Hour | 0 | 23 |  | h | int
HOLDING_REGISTER | Read | 4039 |  | Boiler | Control Type | 0 | 4 | 0-None 1-Safe 2-Ems 3-7Pole 4-Substation |  | int
HOLDING_REGISTER | Write | 4043 |  | AlternativeHeatSource | Operation Mode Request Auto Day | 20 | 99 |  | °C | int
HOLDING_REGISTER | Write | 4044 |  | AlternativeHeatSource | Operation Mode Request Auto Night | 20 | 99 |  | °C | int
HOLDING_REGISTER | Write | 4045 |  | AlternativeHeatSource | Operation Mode Request Manual Day | 20 | 99 |  | °C | int
HOLDING_REGISTER | Write | 4046 |  | AlternativeHeatSource | Operation Mode Request Manual Night | 20 | 99 |  | °C | int
HOLDING_REGISTER | Write | 4047 |  | AlternativeHeatSource | Operation Mode Request Holiday | 20 | 99 |  | °C | int
HOLDING_REGISTER | Write | 4048 |  | AlternativeHeatSource | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 4049 |  | AlternativeHeatSource | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 4050 |  | AlternativeHeatSource | Return Control Setpoint User | 10 | 70 |  | °C | int
HOLDING_REGISTER | Write | 4057 |  | HydraulicCircuit Zm | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 4058 |  | HydraulicCircuit Zm | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 4059 |  | HydraulicCircuit Zm | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4060 |  | HydraulicCircuit Zm | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4061 |  | HydraulicCircuit Zm | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4062 |  | HydraulicCircuit Zm | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4063 |  | HydraulicCircuit Zm | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4064 |  | HydraulicCircuit Zm | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 4070 |  | HydraulicCircuit 1 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 4071 |  | HydraulicCircuit 1 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 4072 |  | HydraulicCircuit 1 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4073 |  | HydraulicCircuit 1 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4074 |  | HydraulicCircuit 1 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4075 |  | HydraulicCircuit 1 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4076 |  | HydraulicCircuit 1 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4077 |  | HydraulicCircuit 1 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 4083 |  | HydraulicCircuit 2 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 4084 |  | HydraulicCircuit 2 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 4085 |  | HydraulicCircuit 2 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4086 |  | HydraulicCircuit 2 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4087 |  | HydraulicCircuit 2 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4088 |  | HydraulicCircuit 2 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4089 |  | HydraulicCircuit 2 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4090 |  | HydraulicCircuit 2 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 4096 |  | HydraulicCircuit 3 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 4097 |  | HydraulicCircuit 3 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 4098 |  | HydraulicCircuit 3 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4099 |  | HydraulicCircuit 3 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4100 |  | HydraulicCircuit 3 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4101 |  | HydraulicCircuit 3 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4102 |  | HydraulicCircuit 3 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4103 |  | HydraulicCircuit 3 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 4109 |  | HydraulicCircuit 4 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 4110 |  | HydraulicCircuit 4 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 4111 |  | HydraulicCircuit 4 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4112 |  | HydraulicCircuit 4 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4113 |  | HydraulicCircuit 4 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4114 |  | HydraulicCircuit 4 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4115 |  | HydraulicCircuit 4 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4116 |  | HydraulicCircuit 4 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 4122 |  | HydraulicCircuit 5 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 4123 |  | HydraulicCircuit 5 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 4124 |  | HydraulicCircuit 5 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4125 |  | HydraulicCircuit 5 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4126 |  | HydraulicCircuit 5 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4127 |  | HydraulicCircuit 5 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4128 |  | HydraulicCircuit 5 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4129 |  | HydraulicCircuit 5 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 4135 |  | HydraulicCircuit 6 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 4136 |  | HydraulicCircuit 6 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 4137 |  | HydraulicCircuit 6 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4138 |  | HydraulicCircuit 6 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4139 |  | HydraulicCircuit 6 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4140 |  | HydraulicCircuit 6 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4141 |  | HydraulicCircuit 6 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4142 |  | HydraulicCircuit 6 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 4148 |  | HydraulicCircuit 7 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 4149 |  | HydraulicCircuit 7 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 4150 |  | HydraulicCircuit 7 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4151 |  | HydraulicCircuit 7 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4152 |  | HydraulicCircuit 7 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4153 |  | HydraulicCircuit 7 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4154 |  | HydraulicCircuit 7 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4155 |  | HydraulicCircuit 7 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 4161 |  | HydraulicCircuit 8 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 4162 |  | HydraulicCircuit 8 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 4163 |  | HydraulicCircuit 8 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4164 |  | HydraulicCircuit 8 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4165 |  | HydraulicCircuit 8 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4166 |  | HydraulicCircuit 8 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4167 |  | HydraulicCircuit 8 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4168 |  | HydraulicCircuit 8 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 4201 |  | Heat Pump | Heat demand source | 0 | 2 | 0-Scheduler 1-System 2-Max_system_scheduler |  | int
HOLDING_REGISTER | Read | 4421 |  | Fresh Water Characteristics 3 | DHU Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 4422 |  | Fresh Water Characteristics 3 | Extra Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 4423 |  | Fresh Water Characteristics 3 | Maximum DHW Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 4424 |  | Fresh Water Characteristics 3 | On High Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 4425 |  | Fresh Water Characteristics 3 | On Low Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 4426 |  | Fresh Water Characteristics 3 | Fresh Water Type | 0 | 3 | 0-15/20l/min 1-27l/min 2-40l/min 3-60l/min |  | int
HOLDING_REGISTER | Read | 4427 |  | Fresh Water Characteristics 3 | Enable Alarm Output | 0 | 2 | 0-No 1-Yes 2-Inverted |  | int
HOLDING_REGISTER | Read | 4428 |  | Fresh Water Characteristics 3 | Buffer Cylinder Temperature Offset |  |  |  | K | int
HOLDING_REGISTER | Read | 4429 |  | Fresh Water Characteristics 3 | hrBitblock |  |  |  |  | int
| Read |  | 0 | Fresh Water | Buffer Cylinder Temperature Optimization Enabled |  |  |  |  | bit
| Read |  | 1 | Fresh Water | Impulse Enabled |  |  |  |  | bit
| Read |  | 2 | Fresh Water | Time Program Enabled |  |  |  |  | bit
HOLDING_REGISTER | Read | 4430 |  | Fresh Water Characteristics 3 | Minimum Buffer Cylinder Temperature Offset |  |  |  | K | int
HOLDING_REGISTER | Read | 4431 |  | Fresh Water Characteristics 2 | Circulation Pump Runs per Hour | 0 | 7 | 0-Undefined 1-1x3_minutes/h 2-2x3_minutes/h 3-3x3_minutes/h 4-4x3_minutes/h 5-5x3_minutes/h 6-6x3_minutes/h 7-Permanent |  | int
HOLDING_REGISTER | Read | 4432 |  | Fresh Water Characteristics 2 | Swich Hysteresis |  |  |  | K | int
HOLDING_REGISTER | Read | 4433 |  | Fresh Water Characteristics 2 | Thermal Disinfection Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 4434 |  | Fresh Water Characteristics 2 | Pre Heat Maximum Temperature |  |  |  | °C | int
INPUT_REGISTER | Read | 4000 |  | System | Own Outdoor temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4001 |  | System | Damped Own outdoor temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4004 |  | System | Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4008 |  | System | Active Functions 1 |  |  |  |  | int
INPUT_REGISTER | Read | 4009 |  | System | Active Functions 2 |  |  |  |  | int
INPUT_REGISTER | Read | 4015 |  | DomesticHotWater Zm | Charge Pump Running | 0 | 4 | 0-Stopping 1-Starting 2-Running 3-Off 4-Error |  | int
INPUT_REGISTER | Read | 4016 |  | DomesticHotWater Zm | Circulation Pump Running | 0 | 4 | 0-Stopping 1-Starting 2-Running 3-Off 4-Error |  | int
INPUT_REGISTER | Read | 4017 |  | DomesticHotWater Zm | Hydraulic State | 0 | 7 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Cold_load 6-Post_purge 7-Condense_protection |  | int
INPUT_REGISTER | Read | 4018 |  | DomesticHotWater Zm/Ems | Thermal Disinfection Status | 0 | 3 | 0-Off 1-On 2-Success 3-Error |  | int
INPUT_REGISTER | Read | 4019 |  | DomesticHotWater Zm/Ems | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 4020 |  | DomesticHotWater Zm/Ems | Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4021 |  | DomesticHotWater Zm/Ems | Current Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4031 |  | DomesticHotWater Fm | Charge Pump Running | 0 | 4 | 0-Stopping 1-Starting 2-Running 3-Off 4-Error |  | int
INPUT_REGISTER | Read | 4032 |  | DomesticHotWater Fm | Circulation Pump Running | 0 | 4 | 0-Stopping 1-Starting 2-Running 3-Off 4-Error |  | int
INPUT_REGISTER | Read | 4033 |  | DomesticHotWater Fm | Hydraulic State | 0 | 7 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Cold_load 6-Post_purge 7-Condense_protection |  | int
INPUT_REGISTER | Read | 4034 |  | DomesticHotWater Fm | Thermal Disinfection Status | 0 | 3 | 0-Off 1-On 2-Success 3-Error |  | int
INPUT_REGISTER | Read | 4035 |  | DomesticHotWater Fm | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 4036 |  | DomesticHotWater Fm | Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4037 |  | DomesticHotWater Fm | Current Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER |  | 4047 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 4048 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 4050 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 4052 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 4053 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 4054 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 4055 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 4056 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 4059 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 4060 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER | Read | 4063 |  | AlternativeHeatSource | Operating hours |  |  |  | h | long
INPUT_REGISTER | Read | 4065 |  | AlternativeHeatSource | Heat Source Starts |  |  |  |  | long
INPUT_REGISTER | Read | 4067 |  | AlternativeHeatSource | Heat Source Hours to Maintenance |  |  |  | h | int
INPUT_REGISTER | Read | 4069 |  | AlternativeHeatSource | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
| Read |  | 0 | AlternativeHeatSource | Is Heat Source On |  |  |  |  | bit
| Read |  | 1 | AlternativeHeatSource | Is Heat Source On Request |  |  |  |  | bit
INPUT_REGISTER | Read | 4087 |  | HydraulicCircuit Zm | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4088 |  | HydraulicCircuit Zm | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4089 |  | HydraulicCircuit Zm | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4090 |  | HydraulicCircuit Zm | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4091 |  | HydraulicCircuit Zm | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 4092 |  | HydraulicCircuit Zm | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 4093 |  | HydraulicCircuit Zm | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 4094 |  | HydraulicCircuit Zm | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 4095 |  | HydraulicCircuit Zm | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 4099 |  | HydraulicCircuit 1 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4100 |  | HydraulicCircuit 1 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4101 |  | HydraulicCircuit 1 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4102 |  | HydraulicCircuit 1 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4103 |  | HydraulicCircuit 1 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 4104 |  | HydraulicCircuit 1 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 4105 |  | HydraulicCircuit 1 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 4106 |  | HydraulicCircuit 1 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 4107 |  | HydraulicCircuit 1 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 4112 |  | HydraulicCircuit 2 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4113 |  | HydraulicCircuit 2 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4114 |  | HydraulicCircuit 2 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4115 |  | HydraulicCircuit 2 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4116 |  | HydraulicCircuit 2 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 4117 |  | HydraulicCircuit 2 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 4118 |  | HydraulicCircuit 2 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 4119 |  | HydraulicCircuit 2 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 4120 |  | HydraulicCircuit 2 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 4125 |  | HydraulicCircuit 3 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4126 |  | HydraulicCircuit 3 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4127 |  | HydraulicCircuit 3 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4128 |  | HydraulicCircuit 3 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4129 |  | HydraulicCircuit 3 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 4130 |  | HydraulicCircuit 3 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 4131 |  | HydraulicCircuit 3 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 4132 |  | HydraulicCircuit 3 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 4133 |  | HydraulicCircuit 3 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 4138 |  | HydraulicCircuit 4 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4139 |  | HydraulicCircuit 4 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4140 |  | HydraulicCircuit 4 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4141 |  | HydraulicCircuit 4 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4142 |  | HydraulicCircuit 4 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 4143 |  | HydraulicCircuit 4 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 4144 |  | HydraulicCircuit 4 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 4145 |  | HydraulicCircuit 4 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 4146 |  | HydraulicCircuit 4 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 4151 |  | HydraulicCircuit 5 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4152 |  | HydraulicCircuit 5 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4153 |  | HydraulicCircuit 5 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4154 |  | HydraulicCircuit 5 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4155 |  | HydraulicCircuit 5 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 4156 |  | HydraulicCircuit 5 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 4157 |  | HydraulicCircuit 5 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 4158 |  | HydraulicCircuit 5 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 4159 |  | HydraulicCircuit 5 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 4164 |  | HydraulicCircuit 6 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4165 |  | HydraulicCircuit 6 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4166 |  | HydraulicCircuit 6 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4167 |  | HydraulicCircuit 6 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4168 |  | HydraulicCircuit 6 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 4169 |  | HydraulicCircuit 6 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 4170 |  | HydraulicCircuit 6 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 4171 |  | HydraulicCircuit 6 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 4172 |  | HydraulicCircuit 6 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 4177 |  | HydraulicCircuit 7 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4178 |  | HydraulicCircuit 7 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4179 |  | HydraulicCircuit 7 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4180 |  | HydraulicCircuit 7 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4181 |  | HydraulicCircuit 7 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 4182 |  | HydraulicCircuit 7 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 4183 |  | HydraulicCircuit 7 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 4184 |  | HydraulicCircuit 7 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 4185 |  | HydraulicCircuit 7 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 4190 |  | HydraulicCircuit 8 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4191 |  | HydraulicCircuit 8 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4192 |  | HydraulicCircuit 8 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4193 |  | HydraulicCircuit 8 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4194 |  | HydraulicCircuit 8 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 4195 |  | HydraulicCircuit 8 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 4196 |  | HydraulicCircuit 8 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 4197 |  | HydraulicCircuit 8 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 4198 |  | HydraulicCircuit 8 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 4203 |  | i2c | Global Error State | 0 | 4 | 0-No_Error 1-i2c_driver_error 2-Wrong_Cycle_Time 3-Missing_Module_Slot 4-Module_Slot_Error |  | int
INPUT_REGISTER | Read | 4204 |  | i2c | Slot1 Module Detected |  |  | 0-Unknown 1-None 22-FM_CM 25-FM_SI 28-FM_MM 29-FM_MW 30-FM_AM 31-FM_CM2 |  | int
INPUT_REGISTER | Read | 4205 |  | i2c | Slot1 Error State |  |  | 0-No_Error 1-No_Response 2-Wrong_Module 3-Unsupported_Module 4-Internal_Sw_Error 5-Communication_Failed 6-Internal_Module_Error 7-Module_Not_Supported_Current_Variant 8-Module_Not_Suppported_In_Slot 9-Module_Count_Too_High 10-Module_Not_Supported_With_Connected_Boiler_Type |  | int
INPUT_REGISTER | Read | 4206 |  | i2c | Slot2 Module Detected |  |  | 0-Unknown 1-None 22-FM_CM 25-FM_SI 28-FM_MM 29-FM_MW 30-FM_AM 31-FM_CM2 |  | int
INPUT_REGISTER | Read | 4207 |  | i2c | Slot2 Error State |  |  | 0-No_Error 1-No_Response 2-Wrong_Module 3-Unsupported_Module 4-Internal_Sw_Error 5-Communication_Failed 6-Internal_Module_Error 7-Module_Not_Supported_Current_Variant 8-Module_Not_Suppported_In_Slot 9-Module_Count_Too_High 10-Module_Not_Supported_With_Connected_Boiler_Type |  | int
INPUT_REGISTER | Read | 4208 |  | i2c | Slot3 Module Detected |  |  | 0-Unknown 1-None 22-FM_CM 25-FM_SI 28-FM_MM 29-FM_MW 30-FM_AM 31-FM_CM2 |  | int
INPUT_REGISTER | Read | 4209 |  | i2c | Slot3 Error State |  |  | 0-No_Error 1-No_Response 2-Wrong_Module 3-Unsupported_Module 4-Internal_Sw_Error 5-Communication_Failed 6-Internal_Module_Error 7-Module_Not_Supported_Current_Variant 8-Module_Not_Suppported_In_Slot 9-Module_Count_Too_High 10-Module_Not_Supported_With_Connected_Boiler_Type |  | int
INPUT_REGISTER | Read | 4210 |  | i2c | Slot4 Module Detected |  |  | 0-Unknown 1-None 22-FM_CM 25-FM_SI 28-FM_MM 29-FM_MW 30-FM_AM 31-FM_CM2 |  | int
INPUT_REGISTER | Read | 4211 |  | i2c | Slot4 Error State |  |  | 0-No_Error 1-No_Response 2-Wrong_Module 3-Unsupported_Module 4-Internal_Sw_Error 5-Communication_Failed 6-Internal_Module_Error 7-Module_Not_Supported_Current_Variant 8-Module_Not_Suppported_In_Slot 9-Module_Count_Too_High 10-Module_Not_Supported_With_Connected_Boiler_Type |  | int
INPUT_REGISTER | Read | 4212 |  | i2c | Slot A Module Detected |  |  | 0-Unknown 1-None 26-ZM5313 27-ZM5311 |  | int
INPUT_REGISTER | Read | 4213 |  | i2c | Slot A Error State |  |  | 0-No_Error 1-No_Response 2-Wrong_Module 3-Unsupported_Module 4-Internal_Sw_Error 5-Communication_Failed 6-Internal_Module_Error 7-Module_Not_Supported_Current_Variant 8-Module_Not_Suppported_In_Slot 9-Module_Count_Too_High 10-Module_Not_Supported_With_Connected_Boiler_Type |  | int
INPUT_REGISTER | Read | 4214 |  | i2c | irBitblock |  |  |  |  | int
| Read |  | 0 | i2c | Component Error |  |  |  |  | bit
INPUT_REGISTER | Read | 4225 |  | fm-si | irBitblock |  |  |  |  | int
| Read |  | 0 | fm-si | Input 1 Error |  |  |  |  | bit
| Read |  | 1 | fm-si | Input 2 Error |  |  |  |  | bit
| Read |  | 2 | fm-si | Input 3 Error |  |  |  |  | bit
| Read |  | 3 | fm-si | Input 4 Error |  |  |  |  | bit
| Read |  | 4 | fm-si | Input 5 Error |  |  |  |  | bit
INPUT_REGISTER | Read | 4232 |  | Sdc | Demand Mode (Low Priority) | 0 | 2 | 0-Off 1-Take_Heat 2-Give_Heat |  | int
INPUT_REGISTER | Read | 4233 |  | Sdc | Demand Flow Temp (Low Priority) |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4234 |  | Sdc | Demand Mode (High Priority) | 0 | 2 | 0-Off 1-Take_Heat 2-Give_Heat |  | int
INPUT_REGISTER | Read | 4235 |  | Sdc | Demand Flow Temp (High Priority) |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4239 |  | Heat Pump | System return temperature for HP heating buffer |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4240 |  | Heat Pump | Buffer mid temperature for HP heating buffer |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4241 |  | Heat Pump | Buffer top temperature for HP heating buffer |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4242 |  | Heat Pump | Buffer bottom temperature for HP heating buffer |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4243 |  | Heat Pump | Return temperature FWR |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4244 |  | Heat Pump | Flow temperature FWV |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4245 |  | Heat Pump | Flow temperature HP |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4246 |  | Heat Pump | Return temperature HP |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4247 |  | Heat Pump | HMI State of HP Component | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 4248 |  | Heat Pump | HP current heat output |  |  |  | kW | signed int | x10
INPUT_REGISTER | Read | 4249 |  | Heat Pump | HP current electrical power consumption | 0 | 10000 |  | kW | int | x10
INPUT_REGISTER | Read | 4250 |  | Heat Pump | HP Smart grid mode | 0 | 3 | 0-normal_charging_grid 1-low_charging_grid 2-high_charging_grid 3-free_charging_grid |  | int
INPUT_REGISTER | Read | 4251 |  | Heat Pump | Heat demand temperature set point |  |  |  | °C | int
INPUT_REGISTER | Read | 4252 |  | Heat Pump | heatPumpStatusIrBitblock | 0 |  |  |  | int
INPUT_REGISTER | Read | 4253 |  | Heat Pump | Ambient Temperature HP |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4254 |  | Heat Pump | HP silent mode | 0 | 3 | 0-standard_mode 1-silent_mode 2-super_silent_mode 3-night_mode |  | int
INPUT_REGISTER | Read | 4255 |  | Heat Pump | Heat Pump Heat Request Temperature |  |  |  | °C | int
INPUT_REGISTER | Read | 4256 |  | Heat Pump | heatPumpIrBitblock |  |  |  |  | int
INPUT_REGISTER | Read | 4265 |  | System | Open Notifications Count |  |  |  |  | int
INPUT_REGISTER | Read | 4266 |  | System | Error Key 5 |  |  |  |  | long
INPUT_REGISTER | Read | 4268 |  | System | Error Key 6 |  |  |  |  | long
INPUT_REGISTER | Read | 4270 |  | System | Error Key 7 |  |  |  |  | long
INPUT_REGISTER | Read | 4272 |  | System | Error Key 8 |  |  |  |  | long
INPUT_REGISTER | Read | 4274 |  | System | Error Key 9 |  |  |  |  | long
INPUT_REGISTER | Read | 4276 |  | System | Error Key 10 |  |  |  |  | long
INPUT_REGISTER | Read | 4278 |  | Chp / EC Power | Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4279 |  | Chp / EC Power | Return Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4280 |  | Chp | Flue Gas Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4281 |  | Chp | Motor Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4282 |  | Chp / EC Power | Current Generator Power |  |  |  | kW | int
INPUT_REGISTER | Read | 4283 |  | Chp | Current Power Setpoint |  |  |  | kW | int
INPUT_REGISTER | Read | 4284 |  | Chp / EC Power | Operation Hours |  |  |  | h | long
INPUT_REGISTER | Read | 4286 |  | Chp / EC Power | Number of starts |  |  |  |  | long
INPUT_REGISTER | Read | 4288 |  | Chp / EC Power | Hours to Maintenance |  |  |  | h | int
INPUT_REGISTER | Read | 4290 |  | Chp | Output Power Setpoint |  |  |  | kW | int
INPUT_REGISTER | Read | 4291 |  | Chp | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 4296 |  | Chp | irBitblock |  |  |  |  | int
| Read |  | 0 | Chp | Warning |  |  |  |  | bit
| Read |  | 1 | Chp / EC Power | Malfunction |  |  |  |  | bit
| Read |  | 2 | Chp / EC Power | Controlled Shutdown |  |  |  |  | bit
| Read |  | 3 | Chp / EC Power | Generator On |  |  |  |  | bit
| Read |  | 4 | Chp | Automatic On |  |  |  |  | bit
| Read |  | 5 | Chp / EC Power | Automatic Ready |  |  |  |  | bit
| Read |  | 11 | Chp / EC Power | Output On Request |  |  |  |  | bit
INPUT_REGISTER | Read | 4304 |  | Water Treatment Module | Program Step |  |  | 20-140: Desalination not active 10000-10810: One time desalination 20000-20810: Automatic desalination 30000-30260: Stationary operation |  | int
INPUT_REGISTER | Read | 4305 |  | Water Treatment Module | Temperature Desalinization |  |  |  | °C | int | x10
INPUT_REGISTER | Read | 4306 |  | Water Treatment Module | Volume Flow |  |  |  | L/min | int | x10
INPUT_REGISTER | Read | 4307 |  | Water Treatment Module | Conductivity system |  |  |  | uS/cm | int | x10
INPUT_REGISTER | Read | 4308 |  | Water Treatment Module | Conductivity cartridge |  |  |  | uS/cm | int | x10
INPUT_REGISTER | Read | 4309 |  | Water Treatment Module | Cartridge Capacity |  |  |  | % | int
INPUT_REGISTER | Read | 4313 |  | Solar Data | Collector temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4314 |  | Solar Data | Temperature cylinder bottom |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4315 |  | Solar Data | Solar pump modulation setpoint |  |  |  | % | int
INPUT_REGISTER | Read | 4316 |  | Solar | Solar pump status | 0 | 19 | 1-TestMod 2-BlckProt 3-No heat 4-Ht avail 5-SolOff 6-MaxCyl 7-MaxColl 8-MinColl 9-FrostP 10-VacFct 11-SwChck 12-MixPrio 13-Switch 14-Priority 15-ThermD 16-MixCal 17-MixOpn 18-MixCl 19-MixOff |  | int
INPUT_REGISTER | Read | 4317 |  | Solar Data | Heat exchanger temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4318 |  | Solar Data | Heat exchanger pump modulation setpoint |  |  |  | % | int
INPUT_REGISTER | Read | 4319 |  | Solar | Heat exchanger pump status | 0 | 19 | 1-TestMod 2-BlckProt 3-No heat 4-Ht avail 5-SolOff 6-MaxCyl 7-MaxColl 8-MinColl 9-FrostP 10-VacFct 11-SwChck 12-MixPrio 13-Switch 14-Priority 15-ThermD 16-MixCal 17-MixOpn 18-MixCl 19-MixOff |  | int
INPUT_REGISTER | Read | 4320 |  | Solar Data | Temperature cylinder 3 top |  |  |  | °C | int | x10
INPUT_REGISTER | Read | 4321 |  | Solar Data | Reload pump modulation setpoint |  |  |  | % | int
INPUT_REGISTER | Read | 4322 |  | Solar | Reload pump status | 0 | 19 | 1-TestMod 2-BlckProt 3-No heat 4-Ht avail 5-SolOff 6-MaxCyl 7-MaxColl 8-MinColl 9-FrostP 10-VacFct 11-SwChck 12-MixPrio 13-Switch 14-Priority 15-ThermD 16-MixCal 17-MixOpn 18-MixCl 19-MixOff |  | int
INPUT_REGISTER | Read | 4323 |  | Solar | Pump therm. disinfect. status | 0 | 19 | 1-TestMod 2-BlckProt 3-No heat 4-Ht avail 5-SolOff 6-MaxCyl 7-MaxColl 8-MinColl 9-FrostP 10-VacFct 11-SwChck 12-MixPrio 13-Switch 14-Priority 15-ThermD 16-MixCal 17-MixOpn 18-MixCl 19-MixOff |  | int
INPUT_REGISTER | Read | 4324 |  | Solar Yield | Flow temperature heat meter |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4325 |  | Solar Yield | Return temperature heat meter |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4326 |  | Solar Yield | Heat count pulse counter | 0 | 15 |  |  | int
INPUT_REGISTER | Read | 4327 |  | Solar Yield | Solar yield per month |  |  |  | kWh | long | x10
INPUT_REGISTER | Read | 4329 |  | Solar Yield | Solar yield per year |  |  |  | kWh | long | x10
INPUT_REGISTER | Read | 4331 |  | Solar Yield | Last hour solar yield |  |  |  | kWh | long | x10
INPUT_REGISTER | Read | 4333 |  | Solar Yield | Solar yield per day |  |  |  | kWh | long | x10
INPUT_REGISTER | Read | 4335 |  | Solar Yield | Solar yield since installation |  |  |  | kWh | long | x10
INPUT_REGISTER | Read | 4337 |  | Solar | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 4338 |  | Solar Data | Hydraulic configuration |  |  |  |  | int
| Read |  | 0 | Solar | Option 1 active |  |  |  |  | bit
| Read |  | 1 | Solar | Option A active |  |  |  |  | bit
| Read |  | 2 | Solar | Option B active |  |  |  |  | bit
| Read |  | 3 | Solar | Option C active |  |  |  |  | bit
| Read |  | 4 | Solar | Option D active |  |  |  |  | bit
| Read |  | 5 | Solar | Option E active |  |  |  |  | bit
| Read |  | 6 | Solar | Option F active |  |  |  |  | bit
| Read |  | 7 | Solar | Option G active |  |  |  |  | bit
| Read |  | 8 | Solar | Option H active |  |  |  |  | bit
| Read |  | 9 | Solar | Option I active |  |  |  |  | bit
| Read |  | 10 | Solar | Option J active |  |  |  |  | bit
| Read |  | 11 | Solar | Option K active |  |  |  |  | bit
| Read |  | 12 | Solar | Option L active |  |  |  |  | bit
| Read |  | 13 | Solar | Option M active |  |  |  |  | bit
| Read |  | 14 | Solar | Option N active |  |  |  |  | bit
| Read |  | 15 | Solar | Option P active |  |  |  |  | bit
INPUT_REGISTER | Read | 4339 |  | Solar Data | irBitblock |  |  |  |  | int
| Read |  | 0 | Solar | Is Active |  |  |  |  | bit
INPUT_REGISTER |  | 4400 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 4401 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 4402 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 4403 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 4404 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 4405 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 4406 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 4407 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 4408 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 4409 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 4410 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 4411 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 4412 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 4413 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER | Read | 4422 |  | Energy Monitoring | Heat Output |  |  |  | kW | signed int | x10
INPUT_REGISTER | Read | 4423 |  | Energy Monitoring | Gas Consumption (LCV) |  |  |  | kW | signed int | x10
INPUT_REGISTER | Read | 4425 |  | Energy Monitoring | Electrical Power |  |  |  | W | int
INPUT_REGISTER | Read | 4430 |  | Fresh Water Characteristics 1 | DHW Out Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4431 |  | Fresh Water Characteristics 1 | DHW Volume Flow |  |  |  | L/min | signed int | x10
INPUT_REGISTER | Read | 4432 |  | Fresh Water Characteristics 1 | Prim In Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4433 |  | Fresh Water Characteristics 1 | DHW In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4434 |  | Fresh Water Characteristics 1 | Primary Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 4435 |  | Fresh Water Characteristics 1 | Request DHW Out Temperature |  |  |  | °C | int
INPUT_REGISTER | Read | 4436 |  | Fresh Water Characteristics 1 | Status Request DHW Out Temperature | 0 | 9 | 0-Off 1-DHWRed 2-DHW 3-Sol_red 4-Once_on 5-Therm_d 6-DlyHtUp 7-Preheat_start 8-Preheat_normal 9-No_eq |  | int
INPUT_REGISTER | Read | 4437 |  | Fresh Water Characteristics 2 | Circulation Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 4438 |  | Fresh Water Characteristics 2 | Status Circulation Pump | 0 | 8 | 0-Undefined 1-Test 2-BlckProt 3-No_req 4-AutoOff 5-AutoOn 6-Therm_d 7-Sys_Off 8-DlyHtUp |  | int
INPUT_REGISTER | Read | 4439 |  | Fresh Water Characteristics 2 | Return Valve Modulation Request |  |  |  | % | int
INPUT_REGISTER | Read | 4440 |  | Fresh Water Characteristics 2 | Valve State | 0 | 5 | 0-Undefined 1-TestMod 2-BlckProt 3-Mix_cl 4-Mix_opn 5-Sys_Off |  | int
INPUT_REGISTER | Read | 4441 |  | Fresh Water Characteristics 2 | Return Valve Buffer Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4442 |  | Fresh Water Characteristics 2 | Disinfection Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 4443 |  | Fresh Water Characteristics 2 | Pump State | 0 | 5 | 0-Undefined 1-TestMod 2-BlckPro 3-No_eq 4-Ht_req 5-Sys_Off |  | int
INPUT_REGISTER | Read | 4444 |  | Fresh Water Characteristics 1 | DHW Valve Power |  |  |  | % | int
INPUT_REGISTER | Read | 4445 |  | Fresh Water Characteristics 2 | Total Flow |  |  |  | L/min | int | x10
INPUT_REGISTER | Read | 4446 |  | Fresh Water 2 | Module 2 DHW Out Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4447 |  | Fresh Water 2 | Module 2 DHW Volume Flow |  |  |  | L/min | signed int | x10
INPUT_REGISTER | Read | 4448 |  | Fresh Water 2 | Module 2 Prim In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4449 |  | Fresh Water 2 | Module 2 DHW In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4450 |  | Fresh Water 2 | Module 2 DHW Valve Power |  |  |  | % | int
INPUT_REGISTER | Read | 4451 |  | Fresh Water 2 | Module 2 Prim Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 4452 |  | Fresh Water 2 | Module 2 Status Prim Pump |  |  |  |  | int
INPUT_REGISTER | Read | 4453 |  | Fresh Water 3 | Module 3 DHW Out Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4454 |  | Fresh Water 3 | Module 3 DHW Volume Flow |  |  |  | L/min | signed int | x10
INPUT_REGISTER | Read | 4455 |  | Fresh Water 3 | Module 3 Prim In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4456 |  | Fresh Water 3 | Module 3 DHW In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4457 |  | Fresh Water 3 | Module 3 DHW Valve Power |  |  |  | % | int
INPUT_REGISTER | Read | 4458 |  | Fresh Water 3 | Module 3 Prim Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 4459 |  | Fresh Water 3 | Module 3 Status Prim Pump |  |  |  |  | int
INPUT_REGISTER | Read | 4460 |  | Fresh Water 4 | Module 4 DHW Out Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4461 |  | Fresh Water 4 | Module 4 DHW Volume Flow |  |  |  | L/min | signed int | x10
INPUT_REGISTER | Read | 4462 |  | Fresh Water 4 | Module 4 Prim In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4463 |  | Fresh Water 4 | Module 4 DHW In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4464 |  | Fresh Water 4 | Module 4 DHW ValvePower |  |  |  | % | int
INPUT_REGISTER | Read | 4465 |  | Fresh Water 4 | Module 4 Prim Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 4466 |  | Fresh Water 4 | Module 4 Status Primary Pump |  |  |  |  | int
INPUT_REGISTER | Read | 4467 |  | Fresh Water | Fresh Water Hmi State |  |  |  |  | int
INPUT_REGISTER | Read | 4468 |  | Fresh Water Characteristics 3 | Fresh Water Configurations |  |  |  |  | int
| Read |  | 0 | Fresh Water | Option 2 active |  |  |  |  | bit
| Read |  | 1 | Fresh Water | Option A active |  |  |  |  | bit
| Read |  | 2 | Fresh Water | Option B active |  |  |  |  | bit
| Read |  | 3 | Fresh Water | Option C active |  |  |  |  | bit
| Read |  | 4 | Fresh Water | Option D active |  |  |  |  | bit
| Read |  | 5 | Fresh Water | Option E active |  |  |  |  | bit
| Read |  | 6 | Fresh Water | Option E active cascade module 2 active |  |  |  |  | bit
| Read |  | 7 | Fresh Water | Option E active cascade module 3 active |  |  |  |  | bit
| Read |  | 8 | Fresh Water | Option E active cascade module 4 active |  |  |  |  | bit
| Read |  | 9 | Fresh Water | Is Active |  |  |  |  | bit
INPUT_REGISTER | Read | 4476 |  | System | Error Key 1 |  |  |  |  | long
INPUT_REGISTER | Read | 4478 |  | System | Error Key 2 |  |  |  |  | long
INPUT_REGISTER | Read | 4480 |  | System | Error Key 3 |  |  |  |  | long
INPUT_REGISTER | Read | 4482 |  | System | Error Key 4 |  |  |  |  | long
INPUT_REGISTER | Read | 4484 |  | System | Error 1 Extra Info (MSB) |  |  |  |  | long
INPUT_REGISTER | Read | 4486 |  | System | Error 1 Extra Info (LSB) |  |  |  |  | long
INPUT_REGISTER | Read | 4488 |  | System | Error 2 Extra Info (MSB) |  |  |  |  | long
INPUT_REGISTER | Read | 4490 |  | System | Error 2 Extra Info (LSB) |  |  |  |  | long
INPUT_REGISTER | Read | 4492 |  | System | Error 3 Extra Info (MSB) |  |  |  |  | long
INPUT_REGISTER | Read | 4494 |  | System | Error 3 Extra Info (LSB) |  |  |  |  | long
INPUT_REGISTER | Read | 4496 |  | System | Error 4 Extra Info (MSB) |  |  |  |  | long
INPUT_REGISTER | Read | 4498 |  | System | Error 4 Extra Info (LSB) |  |  |  |  | long

## Slave09
Register Type | Permissions | Address | Bitblock Bit | Component | Name | Min | Max | Range | Unit | DataType | Float to Int Factor
HOLDING_REGISTER | Write | 4507 |  | DomesticHotWater Zm/Ems | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 4508 |  | DomesticHotWater Zm/Ems | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 4509 |  | DomesticHotWater Zm/Ems | Thermal Disinfection Setpoint | 65 | 75 |  | °C | int | x10
HOLDING_REGISTER | Write | 4510 |  | DomesticHotWater Zm | Setpoint Auto Day | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 4511 |  | DomesticHotWater Zm | Setpoint Auto Night | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 4512 |  | DomesticHotWater Zm | Setpoint Manual Day | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 4513 |  | DomesticHotWater Zm | Setpoint Manual Night | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 4514 |  | DomesticHotWater Zm | Setpoint Holiday | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 4515 |  | DomesticHotWater Zm/Ems | Circulation Pump Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 4516 |  | DomesticHotWater Zm/Ems | Circulation Pump Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 4517 |  | DomesticHotWater Zm/Ems | Disinfection Frequency | 0 | 7 | 0-Daily 1-Monday 2-Tuesday 3-Wednesday 4-Thursday 5-Friday 6-Saturday 7-Sunday |  | int
HOLDING_REGISTER | Write | 4518 |  | DomesticHotWater Zm/Ems | Disinfection Start Hour | 0 | 23 |  | h | int
HOLDING_REGISTER | Write | 4521 |  | DomesticHotWater Fm | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 4522 |  | DomesticHotWater Fm | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 4523 |  | DomesticHotWater Fm | Thermal Disinfection Setpoint | 65 | 75 |  | °C | int | x10
HOLDING_REGISTER | Write | 4524 |  | DomesticHotWater Fm | Setpoint Auto Day | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 4525 |  | DomesticHotWater Fm | Setpoint Auto Night | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 4526 |  | DomesticHotWater Fm | Setpoint Manual Day | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 4527 |  | DomesticHotWater Fm | Setpoint Manual Night | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 4528 |  | DomesticHotWater Fm | Setpoint Holiday | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 4529 |  | DomesticHotWater Fm | Circulation Pump Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 4530 |  | DomesticHotWater Fm | Circulation Pump Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 4531 |  | DomesticHotWater Fm | Disinfection Frequency | 0 | 7 | 0-Daily 1-Monday 2-Tuesday 3-Wednesday 4-Thursday 5-Friday 6-Saturday 7-Sunday |  | int
HOLDING_REGISTER | Write | 4532 |  | DomesticHotWater Fm | Disinfection Start Hour | 0 | 23 |  | h | int
HOLDING_REGISTER | Read | 4539 |  | Boiler | Control Type | 0 | 4 | 0-None 1-Safe 2-Ems 3-7Pole 4-Substation |  | int
HOLDING_REGISTER | Write | 4543 |  | AlternativeHeatSource | Operation Mode Request Auto Day | 20 | 99 |  | °C | int
HOLDING_REGISTER | Write | 4544 |  | AlternativeHeatSource | Operation Mode Request Auto Night | 20 | 99 |  | °C | int
HOLDING_REGISTER | Write | 4545 |  | AlternativeHeatSource | Operation Mode Request Manual Day | 20 | 99 |  | °C | int
HOLDING_REGISTER | Write | 4546 |  | AlternativeHeatSource | Operation Mode Request Manual Night | 20 | 99 |  | °C | int
HOLDING_REGISTER | Write | 4547 |  | AlternativeHeatSource | Operation Mode Request Holiday | 20 | 99 |  | °C | int
HOLDING_REGISTER | Write | 4548 |  | AlternativeHeatSource | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 4549 |  | AlternativeHeatSource | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 4550 |  | AlternativeHeatSource | Return Control Setpoint User | 10 | 70 |  | °C | int
HOLDING_REGISTER | Write | 4557 |  | HydraulicCircuit Zm | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 4558 |  | HydraulicCircuit Zm | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 4559 |  | HydraulicCircuit Zm | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4560 |  | HydraulicCircuit Zm | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4561 |  | HydraulicCircuit Zm | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4562 |  | HydraulicCircuit Zm | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4563 |  | HydraulicCircuit Zm | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4564 |  | HydraulicCircuit Zm | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 4570 |  | HydraulicCircuit 1 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 4571 |  | HydraulicCircuit 1 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 4572 |  | HydraulicCircuit 1 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4573 |  | HydraulicCircuit 1 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4574 |  | HydraulicCircuit 1 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4575 |  | HydraulicCircuit 1 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4576 |  | HydraulicCircuit 1 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4577 |  | HydraulicCircuit 1 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 4583 |  | HydraulicCircuit 2 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 4584 |  | HydraulicCircuit 2 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 4585 |  | HydraulicCircuit 2 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4586 |  | HydraulicCircuit 2 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4587 |  | HydraulicCircuit 2 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4588 |  | HydraulicCircuit 2 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4589 |  | HydraulicCircuit 2 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4590 |  | HydraulicCircuit 2 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 4596 |  | HydraulicCircuit 3 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 4597 |  | HydraulicCircuit 3 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 4598 |  | HydraulicCircuit 3 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4599 |  | HydraulicCircuit 3 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4600 |  | HydraulicCircuit 3 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4601 |  | HydraulicCircuit 3 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4602 |  | HydraulicCircuit 3 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4603 |  | HydraulicCircuit 3 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 4609 |  | HydraulicCircuit 4 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 4610 |  | HydraulicCircuit 4 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 4611 |  | HydraulicCircuit 4 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4612 |  | HydraulicCircuit 4 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4613 |  | HydraulicCircuit 4 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4614 |  | HydraulicCircuit 4 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4615 |  | HydraulicCircuit 4 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4616 |  | HydraulicCircuit 4 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 4622 |  | HydraulicCircuit 5 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 4623 |  | HydraulicCircuit 5 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 4624 |  | HydraulicCircuit 5 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4625 |  | HydraulicCircuit 5 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4626 |  | HydraulicCircuit 5 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4627 |  | HydraulicCircuit 5 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4628 |  | HydraulicCircuit 5 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4629 |  | HydraulicCircuit 5 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 4635 |  | HydraulicCircuit 6 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 4636 |  | HydraulicCircuit 6 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 4637 |  | HydraulicCircuit 6 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4638 |  | HydraulicCircuit 6 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4639 |  | HydraulicCircuit 6 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4640 |  | HydraulicCircuit 6 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4641 |  | HydraulicCircuit 6 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4642 |  | HydraulicCircuit 6 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 4648 |  | HydraulicCircuit 7 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 4649 |  | HydraulicCircuit 7 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 4650 |  | HydraulicCircuit 7 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4651 |  | HydraulicCircuit 7 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4652 |  | HydraulicCircuit 7 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4653 |  | HydraulicCircuit 7 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4654 |  | HydraulicCircuit 7 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4655 |  | HydraulicCircuit 7 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 4661 |  | HydraulicCircuit 8 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 4662 |  | HydraulicCircuit 8 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 4663 |  | HydraulicCircuit 8 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4664 |  | HydraulicCircuit 8 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4665 |  | HydraulicCircuit 8 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4666 |  | HydraulicCircuit 8 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4667 |  | HydraulicCircuit 8 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 4668 |  | HydraulicCircuit 8 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 4701 |  | Heat Pump | Heat demand source | 0 | 2 | 0-Scheduler 1-System 2-Max_system_scheduler |  | int
HOLDING_REGISTER | Read | 4921 |  | Fresh Water Characteristics 3 | DHU Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 4922 |  | Fresh Water Characteristics 3 | Extra Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 4923 |  | Fresh Water Characteristics 3 | Maximum DHW Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 4924 |  | Fresh Water Characteristics 3 | On High Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 4925 |  | Fresh Water Characteristics 3 | On Low Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 4926 |  | Fresh Water Characteristics 3 | Fresh Water Type | 0 | 3 | 0-15/20l/min 1-27l/min 2-40l/min 3-60l/min |  | int
HOLDING_REGISTER | Read | 4927 |  | Fresh Water Characteristics 3 | Enable Alarm Output | 0 | 2 | 0-No 1-Yes 2-Inverted |  | int
HOLDING_REGISTER | Read | 4928 |  | Fresh Water Characteristics 3 | Buffer Cylinder Temperature Offset |  |  |  | K | int
HOLDING_REGISTER | Read | 4929 |  | Fresh Water Characteristics 3 | hrBitblock |  |  |  |  | int
| Read |  | 0 | Fresh Water | Buffer Cylinder Temperature Optimization Enabled |  |  |  |  | bit
| Read |  | 1 | Fresh Water | Impulse Enabled |  |  |  |  | bit
| Read |  | 2 | Fresh Water | Time Program Enabled |  |  |  |  | bit
HOLDING_REGISTER | Read | 4930 |  | Fresh Water Characteristics 3 | Minimum Buffer Cylinder Temperature Offset |  |  |  | K | int
HOLDING_REGISTER | Read | 4931 |  | Fresh Water Characteristics 2 | Circulation Pump Runs per Hour | 0 | 7 | 0-Undefined 1-1x3_minutes/h 2-2x3_minutes/h 3-3x3_minutes/h 4-4x3_minutes/h 5-5x3_minutes/h 6-6x3_minutes/h 7-Permanent |  | int
HOLDING_REGISTER | Read | 4932 |  | Fresh Water Characteristics 2 | Swich Hysteresis |  |  |  | K | int
HOLDING_REGISTER | Read | 4933 |  | Fresh Water Characteristics 2 | Thermal Disinfection Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 4934 |  | Fresh Water Characteristics 2 | Pre Heat Maximum Temperature |  |  |  | °C | int
INPUT_REGISTER | Read | 4500 |  | System | Own Outdoor temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4501 |  | System | Damped Own outdoor temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4504 |  | System | Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4508 |  | System | Active Functions 1 |  |  |  |  | int
INPUT_REGISTER | Read | 4509 |  | System | Active Functions 2 |  |  |  |  | int
INPUT_REGISTER | Read | 4515 |  | DomesticHotWater Zm | Charge Pump Running | 0 | 4 | 0-Stopping 1-Starting 2-Running 3-Off 4-Error |  | int
INPUT_REGISTER | Read | 4516 |  | DomesticHotWater Zm | Circulation Pump Running | 0 | 4 | 0-Stopping 1-Starting 2-Running 3-Off 4-Error |  | int
INPUT_REGISTER | Read | 4517 |  | DomesticHotWater Zm | Hydraulic State | 0 | 7 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Cold_load 6-Post_purge 7-Condense_protection |  | int
INPUT_REGISTER | Read | 4518 |  | DomesticHotWater Zm/Ems | Thermal Disinfection Status | 0 | 3 | 0-Off 1-On 2-Success 3-Error |  | int
INPUT_REGISTER | Read | 4519 |  | DomesticHotWater Zm/Ems | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 4520 |  | DomesticHotWater Zm/Ems | Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4521 |  | DomesticHotWater Zm/Ems | Current Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4531 |  | DomesticHotWater Fm | Charge Pump Running | 0 | 4 | 0-Stopping 1-Starting 2-Running 3-Off 4-Error |  | int
INPUT_REGISTER | Read | 4532 |  | DomesticHotWater Fm | Circulation Pump Running | 0 | 4 | 0-Stopping 1-Starting 2-Running 3-Off 4-Error |  | int
INPUT_REGISTER | Read | 4533 |  | DomesticHotWater Fm | Hydraulic State | 0 | 7 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Cold_load 6-Post_purge 7-Condense_protection |  | int
INPUT_REGISTER | Read | 4534 |  | DomesticHotWater Fm | Thermal Disinfection Status | 0 | 3 | 0-Off 1-On 2-Success 3-Error |  | int
INPUT_REGISTER | Read | 4535 |  | DomesticHotWater Fm | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 4536 |  | DomesticHotWater Fm | Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4537 |  | DomesticHotWater Fm | Current Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER |  | 4547 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 4548 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 4550 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 4552 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 4553 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 4554 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 4555 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 4556 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 4559 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 4560 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER | Read | 4563 |  | AlternativeHeatSource | Operating hours |  |  |  | h | long
INPUT_REGISTER | Read | 4565 |  | AlternativeHeatSource | Heat Source Starts |  |  |  |  | long
INPUT_REGISTER | Read | 4567 |  | AlternativeHeatSource | Heat Source Hours to Maintenance |  |  |  | h | int
INPUT_REGISTER | Read | 4569 |  | AlternativeHeatSource | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
| Read |  | 0 | AlternativeHeatSource | Is Heat Source On |  |  |  |  | bit
| Read |  | 1 | AlternativeHeatSource | Is Heat Source On Request |  |  |  |  | bit
INPUT_REGISTER | Read | 4587 |  | HydraulicCircuit Zm | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4588 |  | HydraulicCircuit Zm | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4589 |  | HydraulicCircuit Zm | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4590 |  | HydraulicCircuit Zm | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4591 |  | HydraulicCircuit Zm | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 4592 |  | HydraulicCircuit Zm | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 4593 |  | HydraulicCircuit Zm | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 4594 |  | HydraulicCircuit Zm | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 4595 |  | HydraulicCircuit Zm | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 4599 |  | HydraulicCircuit 1 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4600 |  | HydraulicCircuit 1 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4601 |  | HydraulicCircuit 1 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4602 |  | HydraulicCircuit 1 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4603 |  | HydraulicCircuit 1 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 4604 |  | HydraulicCircuit 1 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 4605 |  | HydraulicCircuit 1 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 4606 |  | HydraulicCircuit 1 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 4607 |  | HydraulicCircuit 1 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 4612 |  | HydraulicCircuit 2 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4613 |  | HydraulicCircuit 2 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4614 |  | HydraulicCircuit 2 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4615 |  | HydraulicCircuit 2 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4616 |  | HydraulicCircuit 2 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 4617 |  | HydraulicCircuit 2 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 4618 |  | HydraulicCircuit 2 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 4619 |  | HydraulicCircuit 2 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 4620 |  | HydraulicCircuit 2 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 4625 |  | HydraulicCircuit 3 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4626 |  | HydraulicCircuit 3 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4627 |  | HydraulicCircuit 3 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4628 |  | HydraulicCircuit 3 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4629 |  | HydraulicCircuit 3 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 4630 |  | HydraulicCircuit 3 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 4631 |  | HydraulicCircuit 3 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 4632 |  | HydraulicCircuit 3 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 4633 |  | HydraulicCircuit 3 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 4638 |  | HydraulicCircuit 4 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4639 |  | HydraulicCircuit 4 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4640 |  | HydraulicCircuit 4 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4641 |  | HydraulicCircuit 4 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4642 |  | HydraulicCircuit 4 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 4643 |  | HydraulicCircuit 4 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 4644 |  | HydraulicCircuit 4 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 4645 |  | HydraulicCircuit 4 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 4646 |  | HydraulicCircuit 4 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 4651 |  | HydraulicCircuit 5 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4652 |  | HydraulicCircuit 5 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4653 |  | HydraulicCircuit 5 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4654 |  | HydraulicCircuit 5 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4655 |  | HydraulicCircuit 5 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 4656 |  | HydraulicCircuit 5 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 4657 |  | HydraulicCircuit 5 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 4658 |  | HydraulicCircuit 5 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 4659 |  | HydraulicCircuit 5 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 4664 |  | HydraulicCircuit 6 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4665 |  | HydraulicCircuit 6 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4666 |  | HydraulicCircuit 6 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4667 |  | HydraulicCircuit 6 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4668 |  | HydraulicCircuit 6 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 4669 |  | HydraulicCircuit 6 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 4670 |  | HydraulicCircuit 6 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 4671 |  | HydraulicCircuit 6 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 4672 |  | HydraulicCircuit 6 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 4677 |  | HydraulicCircuit 7 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4678 |  | HydraulicCircuit 7 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4679 |  | HydraulicCircuit 7 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4680 |  | HydraulicCircuit 7 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4681 |  | HydraulicCircuit 7 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 4682 |  | HydraulicCircuit 7 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 4683 |  | HydraulicCircuit 7 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 4684 |  | HydraulicCircuit 7 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 4685 |  | HydraulicCircuit 7 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 4690 |  | HydraulicCircuit 8 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4691 |  | HydraulicCircuit 8 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4692 |  | HydraulicCircuit 8 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4693 |  | HydraulicCircuit 8 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4694 |  | HydraulicCircuit 8 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 4695 |  | HydraulicCircuit 8 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 4696 |  | HydraulicCircuit 8 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 4697 |  | HydraulicCircuit 8 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 4698 |  | HydraulicCircuit 8 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 4703 |  | i2c | Global Error State | 0 | 4 | 0-No_Error 1-i2c_driver_error 2-Wrong_Cycle_Time 3-Missing_Module_Slot 4-Module_Slot_Error |  | int
INPUT_REGISTER | Read | 4704 |  | i2c | Slot1 Module Detected |  |  | 0-Unknown 1-None 22-FM_CM 25-FM_SI 28-FM_MM 29-FM_MW 30-FM_AM 31-FM_CM2 |  | int
INPUT_REGISTER | Read | 4705 |  | i2c | Slot1 Error State |  |  | 0-No_Error 1-No_Response 2-Wrong_Module 3-Unsupported_Module 4-Internal_Sw_Error 5-Communication_Failed 6-Internal_Module_Error 7-Module_Not_Supported_Current_Variant 8-Module_Not_Suppported_In_Slot 9-Module_Count_Too_High 10-Module_Not_Supported_With_Connected_Boiler_Type |  | int
INPUT_REGISTER | Read | 4706 |  | i2c | Slot2 Module Detected |  |  | 0-Unknown 1-None 22-FM_CM 25-FM_SI 28-FM_MM 29-FM_MW 30-FM_AM 31-FM_CM2 |  | int
INPUT_REGISTER | Read | 4707 |  | i2c | Slot2 Error State |  |  | 0-No_Error 1-No_Response 2-Wrong_Module 3-Unsupported_Module 4-Internal_Sw_Error 5-Communication_Failed 6-Internal_Module_Error 7-Module_Not_Supported_Current_Variant 8-Module_Not_Suppported_In_Slot 9-Module_Count_Too_High 10-Module_Not_Supported_With_Connected_Boiler_Type |  | int
INPUT_REGISTER | Read | 4708 |  | i2c | Slot3 Module Detected |  |  | 0-Unknown 1-None 22-FM_CM 25-FM_SI 28-FM_MM 29-FM_MW 30-FM_AM 31-FM_CM2 |  | int
INPUT_REGISTER | Read | 4709 |  | i2c | Slot3 Error State |  |  | 0-No_Error 1-No_Response 2-Wrong_Module 3-Unsupported_Module 4-Internal_Sw_Error 5-Communication_Failed 6-Internal_Module_Error 7-Module_Not_Supported_Current_Variant 8-Module_Not_Suppported_In_Slot 9-Module_Count_Too_High 10-Module_Not_Supported_With_Connected_Boiler_Type |  | int
INPUT_REGISTER | Read | 4710 |  | i2c | Slot4 Module Detected |  |  | 0-Unknown 1-None 22-FM_CM 25-FM_SI 28-FM_MM 29-FM_MW 30-FM_AM 31-FM_CM2 |  | int
INPUT_REGISTER | Read | 4711 |  | i2c | Slot4 Error State |  |  | 0-No_Error 1-No_Response 2-Wrong_Module 3-Unsupported_Module 4-Internal_Sw_Error 5-Communication_Failed 6-Internal_Module_Error 7-Module_Not_Supported_Current_Variant 8-Module_Not_Suppported_In_Slot 9-Module_Count_Too_High 10-Module_Not_Supported_With_Connected_Boiler_Type |  | int
INPUT_REGISTER | Read | 4712 |  | i2c | Slot A Module Detected |  |  | 0-Unknown 1-None 26-ZM5313 27-ZM5311 |  | int
INPUT_REGISTER | Read | 4713 |  | i2c | Slot A Error State |  |  | 0-No_Error 1-No_Response 2-Wrong_Module 3-Unsupported_Module 4-Internal_Sw_Error 5-Communication_Failed 6-Internal_Module_Error 7-Module_Not_Supported_Current_Variant 8-Module_Not_Suppported_In_Slot 9-Module_Count_Too_High 10-Module_Not_Supported_With_Connected_Boiler_Type |  | int
INPUT_REGISTER | Read | 4714 |  | i2c | irBitblock |  |  |  |  | int
| Read |  | 0 | i2c | Component Error |  |  |  |  | bit
INPUT_REGISTER | Read | 4725 |  | fm-si | irBitblock |  |  |  |  | int
| Read |  | 0 | fm-si | Input 1 Error |  |  |  |  | bit
| Read |  | 1 | fm-si | Input 2 Error |  |  |  |  | bit
| Read |  | 2 | fm-si | Input 3 Error |  |  |  |  | bit
| Read |  | 3 | fm-si | Input 4 Error |  |  |  |  | bit
| Read |  | 4 | fm-si | Input 5 Error |  |  |  |  | bit
INPUT_REGISTER | Read | 4732 |  | Sdc | Demand Mode (Low Priority) | 0 | 2 | 0-Off 1-Take_Heat 2-Give_Heat |  | int
INPUT_REGISTER | Read | 4733 |  | Sdc | Demand Flow Temp (Low Priority) |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4734 |  | Sdc | Demand Mode (High Priority) | 0 | 2 | 0-Off 1-Take_Heat 2-Give_Heat |  | int
INPUT_REGISTER | Read | 4735 |  | Sdc | Demand Flow Temp (High Priority) |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4739 |  | Heat Pump | System return temperature for HP heating buffer |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4740 |  | Heat Pump | Buffer mid temperature for HP heating buffer |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4741 |  | Heat Pump | Buffer top temperature for HP heating buffer |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4742 |  | Heat Pump | Buffer bottom temperature for HP heating buffer |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4743 |  | Heat Pump | Return temperature FWR |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4744 |  | Heat Pump | Flow temperature FWV |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4745 |  | Heat Pump | Flow temperature HP |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4746 |  | Heat Pump | Return temperature HP |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4747 |  | Heat Pump | HMI State of HP Component | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 4748 |  | Heat Pump | HP current heat output |  |  |  | kW | signed int | x10
INPUT_REGISTER | Read | 4749 |  | Heat Pump | HP current electrical power consumption | 0 | 10000 |  | kW | int | x10
INPUT_REGISTER | Read | 4750 |  | Heat Pump | HP Smart grid mode | 0 | 3 | 0-normal_charging_grid 1-low_charging_grid 2-high_charging_grid 3-free_charging_grid |  | int
INPUT_REGISTER | Read | 4751 |  | Heat Pump | Heat demand temperature set point |  |  |  | °C | int
INPUT_REGISTER | Read | 4752 |  | Heat Pump | heatPumpStatusIrBitblock | 0 |  |  |  | int
INPUT_REGISTER | Read | 4753 |  | Heat Pump | Ambient Temperature HP |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4754 |  | Heat Pump | HP silent mode | 0 | 3 | 0-standard_mode 1-silent_mode 2-super_silent_mode 3-night_mode |  | int
INPUT_REGISTER | Read | 4755 |  | Heat Pump | Heat Pump Heat Request Temperature |  |  |  | °C | int
INPUT_REGISTER | Read | 4756 |  | Heat Pump | heatPumpIrBitblock |  |  |  |  | int
INPUT_REGISTER | Read | 4765 |  | System | Open Notifications Count |  |  |  |  | int
INPUT_REGISTER | Read | 4766 |  | System | Error Key 5 |  |  |  |  | long
INPUT_REGISTER | Read | 4768 |  | System | Error Key 6 |  |  |  |  | long
INPUT_REGISTER | Read | 4770 |  | System | Error Key 7 |  |  |  |  | long
INPUT_REGISTER | Read | 4772 |  | System | Error Key 8 |  |  |  |  | long
INPUT_REGISTER | Read | 4774 |  | System | Error Key 9 |  |  |  |  | long
INPUT_REGISTER | Read | 4776 |  | System | Error Key 10 |  |  |  |  | long
INPUT_REGISTER | Read | 4778 |  | Chp / EC Power | Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4779 |  | Chp / EC Power | Return Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4780 |  | Chp | Flue Gas Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4781 |  | Chp | Motor Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4782 |  | Chp / EC Power | Current Generator Power |  |  |  | kW | int
INPUT_REGISTER | Read | 4783 |  | Chp | Current Power Setpoint |  |  |  | kW | int
INPUT_REGISTER | Read | 4784 |  | Chp / EC Power | Operation Hours |  |  |  | h | long
INPUT_REGISTER | Read | 4786 |  | Chp / EC Power | Number of starts |  |  |  |  | long
INPUT_REGISTER | Read | 4788 |  | Chp / EC Power | Hours to Maintenance |  |  |  | h | int
INPUT_REGISTER | Read | 4790 |  | Chp | Output Power Setpoint |  |  |  | kW | int
INPUT_REGISTER | Read | 4791 |  | Chp | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 4796 |  | Chp | irBitblock |  |  |  |  | int
| Read |  | 0 | Chp | Warning |  |  |  |  | bit
| Read |  | 1 | Chp / EC Power | Malfunction |  |  |  |  | bit
| Read |  | 2 | Chp / EC Power | Controlled Shutdown |  |  |  |  | bit
| Read |  | 3 | Chp / EC Power | Generator On |  |  |  |  | bit
| Read |  | 4 | Chp | Automatic On |  |  |  |  | bit
| Read |  | 5 | Chp / EC Power | Automatic Ready |  |  |  |  | bit
| Read |  | 11 | Chp / EC Power | Output On Request |  |  |  |  | bit
INPUT_REGISTER | Read | 4804 |  | Water Treatment Module | Program Step |  |  | 20-140: Desalination not active 10000-10810: One time desalination 20000-20810: Automatic desalination 30000-30260: Stationary operation |  | int
INPUT_REGISTER | Read | 4805 |  | Water Treatment Module | Temperature Desalinization |  |  |  | °C | int | x10
INPUT_REGISTER | Read | 4806 |  | Water Treatment Module | Volume Flow |  |  |  | L/min | int | x10
INPUT_REGISTER | Read | 4807 |  | Water Treatment Module | Conductivity system |  |  |  | uS/cm | int | x10
INPUT_REGISTER | Read | 4808 |  | Water Treatment Module | Conductivity cartridge |  |  |  | uS/cm | int | x10
INPUT_REGISTER | Read | 4809 |  | Water Treatment Module | Cartridge Capacity |  |  |  | % | int
INPUT_REGISTER | Read | 4813 |  | Solar Data | Collector temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4814 |  | Solar Data | Temperature cylinder bottom |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4815 |  | Solar Data | Solar pump modulation setpoint |  |  |  | % | int
INPUT_REGISTER | Read | 4816 |  | Solar | Solar pump status | 0 | 19 | 1-TestMod 2-BlckProt 3-No heat 4-Ht avail 5-SolOff 6-MaxCyl 7-MaxColl 8-MinColl 9-FrostP 10-VacFct 11-SwChck 12-MixPrio 13-Switch 14-Priority 15-ThermD 16-MixCal 17-MixOpn 18-MixCl 19-MixOff |  | int
INPUT_REGISTER | Read | 4817 |  | Solar Data | Heat exchanger temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4818 |  | Solar Data | Heat exchanger pump modulation setpoint |  |  |  | % | int
INPUT_REGISTER | Read | 4819 |  | Solar | Heat exchanger pump status | 0 | 19 | 1-TestMod 2-BlckProt 3-No heat 4-Ht avail 5-SolOff 6-MaxCyl 7-MaxColl 8-MinColl 9-FrostP 10-VacFct 11-SwChck 12-MixPrio 13-Switch 14-Priority 15-ThermD 16-MixCal 17-MixOpn 18-MixCl 19-MixOff |  | int
INPUT_REGISTER | Read | 4820 |  | Solar Data | Temperature cylinder 3 top |  |  |  | °C | int | x10
INPUT_REGISTER | Read | 4821 |  | Solar Data | Reload pump modulation setpoint |  |  |  | % | int
INPUT_REGISTER | Read | 4822 |  | Solar | Reload pump status | 0 | 19 | 1-TestMod 2-BlckProt 3-No heat 4-Ht avail 5-SolOff 6-MaxCyl 7-MaxColl 8-MinColl 9-FrostP 10-VacFct 11-SwChck 12-MixPrio 13-Switch 14-Priority 15-ThermD 16-MixCal 17-MixOpn 18-MixCl 19-MixOff |  | int
INPUT_REGISTER | Read | 4823 |  | Solar | Pump therm. disinfect. status | 0 | 19 | 1-TestMod 2-BlckProt 3-No heat 4-Ht avail 5-SolOff 6-MaxCyl 7-MaxColl 8-MinColl 9-FrostP 10-VacFct 11-SwChck 12-MixPrio 13-Switch 14-Priority 15-ThermD 16-MixCal 17-MixOpn 18-MixCl 19-MixOff |  | int
INPUT_REGISTER | Read | 4824 |  | Solar Yield | Flow temperature heat meter |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4825 |  | Solar Yield | Return temperature heat meter |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4826 |  | Solar Yield | Heat count pulse counter | 0 | 15 |  |  | int
INPUT_REGISTER | Read | 4827 |  | Solar Yield | Solar yield per month |  |  |  | kWh | long | x10
INPUT_REGISTER | Read | 4829 |  | Solar Yield | Solar yield per year |  |  |  | kWh | long | x10
INPUT_REGISTER | Read | 4831 |  | Solar Yield | Last hour solar yield |  |  |  | kWh | long | x10
INPUT_REGISTER | Read | 4833 |  | Solar Yield | Solar yield per day |  |  |  | kWh | long | x10
INPUT_REGISTER | Read | 4835 |  | Solar Yield | Solar yield since installation |  |  |  | kWh | long | x10
INPUT_REGISTER | Read | 4837 |  | Solar | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 4838 |  | Solar Data | Hydraulic configuration |  |  |  |  | int
| Read |  | 0 | Solar | Option 1 active |  |  |  |  | bit
| Read |  | 1 | Solar | Option A active |  |  |  |  | bit
| Read |  | 2 | Solar | Option B active |  |  |  |  | bit
| Read |  | 3 | Solar | Option C active |  |  |  |  | bit
| Read |  | 4 | Solar | Option D active |  |  |  |  | bit
| Read |  | 5 | Solar | Option E active |  |  |  |  | bit
| Read |  | 6 | Solar | Option F active |  |  |  |  | bit
| Read |  | 7 | Solar | Option G active |  |  |  |  | bit
| Read |  | 8 | Solar | Option H active |  |  |  |  | bit
| Read |  | 9 | Solar | Option I active |  |  |  |  | bit
| Read |  | 10 | Solar | Option J active |  |  |  |  | bit
| Read |  | 11 | Solar | Option K active |  |  |  |  | bit
| Read |  | 12 | Solar | Option L active |  |  |  |  | bit
| Read |  | 13 | Solar | Option M active |  |  |  |  | bit
| Read |  | 14 | Solar | Option N active |  |  |  |  | bit
| Read |  | 15 | Solar | Option P active |  |  |  |  | bit
INPUT_REGISTER | Read | 4839 |  | Solar Data | irBitblock |  |  |  |  | int
| Read |  | 0 | Solar | Is Active |  |  |  |  | bit
INPUT_REGISTER |  | 4900 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 4901 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 4902 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 4903 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 4904 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 4905 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 4906 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 4907 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 4908 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 4909 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 4910 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 4911 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 4912 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 4913 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER | Read | 4922 |  | Energy Monitoring | Heat Output |  |  |  | kW | signed int | x10
INPUT_REGISTER | Read | 4923 |  | Energy Monitoring | Gas Consumption (LCV) |  |  |  | kW | signed int | x10
INPUT_REGISTER | Read | 4925 |  | Energy Monitoring | Electrical Power |  |  |  | W | int
INPUT_REGISTER | Read | 4930 |  | Fresh Water Characteristics 1 | DHW Out Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4931 |  | Fresh Water Characteristics 1 | DHW Volume Flow |  |  |  | L/min | signed int | x10
INPUT_REGISTER | Read | 4932 |  | Fresh Water Characteristics 1 | Prim In Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4933 |  | Fresh Water Characteristics 1 | DHW In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4934 |  | Fresh Water Characteristics 1 | Primary Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 4935 |  | Fresh Water Characteristics 1 | Request DHW Out Temperature |  |  |  | °C | int
INPUT_REGISTER | Read | 4936 |  | Fresh Water Characteristics 1 | Status Request DHW Out Temperature | 0 | 9 | 0-Off 1-DHWRed 2-DHW 3-Sol_red 4-Once_on 5-Therm_d 6-DlyHtUp 7-Preheat_start 8-Preheat_normal 9-No_eq |  | int
INPUT_REGISTER | Read | 4937 |  | Fresh Water Characteristics 2 | Circulation Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 4938 |  | Fresh Water Characteristics 2 | Status Circulation Pump | 0 | 8 | 0-Undefined 1-Test 2-BlckProt 3-No_req 4-AutoOff 5-AutoOn 6-Therm_d 7-Sys_Off 8-DlyHtUp |  | int
INPUT_REGISTER | Read | 4939 |  | Fresh Water Characteristics 2 | Return Valve Modulation Request |  |  |  | % | int
INPUT_REGISTER | Read | 4940 |  | Fresh Water Characteristics 2 | Valve State | 0 | 5 | 0-Undefined 1-TestMod 2-BlckProt 3-Mix_cl 4-Mix_opn 5-Sys_Off |  | int
INPUT_REGISTER | Read | 4941 |  | Fresh Water Characteristics 2 | Return Valve Buffer Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4942 |  | Fresh Water Characteristics 2 | Disinfection Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 4943 |  | Fresh Water Characteristics 2 | Pump State | 0 | 5 | 0-Undefined 1-TestMod 2-BlckPro 3-No_eq 4-Ht_req 5-Sys_Off |  | int
INPUT_REGISTER | Read | 4944 |  | Fresh Water Characteristics 1 | DHW Valve Power |  |  |  | % | int
INPUT_REGISTER | Read | 4945 |  | Fresh Water Characteristics 2 | Total Flow |  |  |  | L/min | int | x10
INPUT_REGISTER | Read | 4946 |  | Fresh Water 2 | Module 2 DHW Out Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4947 |  | Fresh Water 2 | Module 2 DHW Volume Flow |  |  |  | L/min | signed int | x10
INPUT_REGISTER | Read | 4948 |  | Fresh Water 2 | Module 2 Prim In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4949 |  | Fresh Water 2 | Module 2 DHW In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4950 |  | Fresh Water 2 | Module 2 DHW Valve Power |  |  |  | % | int
INPUT_REGISTER | Read | 4951 |  | Fresh Water 2 | Module 2 Prim Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 4952 |  | Fresh Water 2 | Module 2 Status Prim Pump |  |  |  |  | int
INPUT_REGISTER | Read | 4953 |  | Fresh Water 3 | Module 3 DHW Out Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4954 |  | Fresh Water 3 | Module 3 DHW Volume Flow |  |  |  | L/min | signed int | x10
INPUT_REGISTER | Read | 4955 |  | Fresh Water 3 | Module 3 Prim In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4956 |  | Fresh Water 3 | Module 3 DHW In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4957 |  | Fresh Water 3 | Module 3 DHW Valve Power |  |  |  | % | int
INPUT_REGISTER | Read | 4958 |  | Fresh Water 3 | Module 3 Prim Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 4959 |  | Fresh Water 3 | Module 3 Status Prim Pump |  |  |  |  | int
INPUT_REGISTER | Read | 4960 |  | Fresh Water 4 | Module 4 DHW Out Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4961 |  | Fresh Water 4 | Module 4 DHW Volume Flow |  |  |  | L/min | signed int | x10
INPUT_REGISTER | Read | 4962 |  | Fresh Water 4 | Module 4 Prim In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4963 |  | Fresh Water 4 | Module 4 DHW In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 4964 |  | Fresh Water 4 | Module 4 DHW ValvePower |  |  |  | % | int
INPUT_REGISTER | Read | 4965 |  | Fresh Water 4 | Module 4 Prim Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 4966 |  | Fresh Water 4 | Module 4 Status Primary Pump |  |  |  |  | int
INPUT_REGISTER | Read | 4967 |  | Fresh Water | Fresh Water Hmi State |  |  |  |  | int
INPUT_REGISTER | Read | 4968 |  | Fresh Water Characteristics 3 | Fresh Water Configurations |  |  |  |  | int
| Read |  | 0 | Fresh Water | Option 2 active |  |  |  |  | bit
| Read |  | 1 | Fresh Water | Option A active |  |  |  |  | bit
| Read |  | 2 | Fresh Water | Option B active |  |  |  |  | bit
| Read |  | 3 | Fresh Water | Option C active |  |  |  |  | bit
| Read |  | 4 | Fresh Water | Option D active |  |  |  |  | bit
| Read |  | 5 | Fresh Water | Option E active |  |  |  |  | bit
| Read |  | 6 | Fresh Water | Option E active cascade module 2 active |  |  |  |  | bit
| Read |  | 7 | Fresh Water | Option E active cascade module 3 active |  |  |  |  | bit
| Read |  | 8 | Fresh Water | Option E active cascade module 4 active |  |  |  |  | bit
| Read |  | 9 | Fresh Water | Is Active |  |  |  |  | bit
INPUT_REGISTER | Read | 4976 |  | System | Error Key 1 |  |  |  |  | long
INPUT_REGISTER | Read | 4978 |  | System | Error Key 2 |  |  |  |  | long
INPUT_REGISTER | Read | 4980 |  | System | Error Key 3 |  |  |  |  | long
INPUT_REGISTER | Read | 4982 |  | System | Error Key 4 |  |  |  |  | long
INPUT_REGISTER | Read | 4984 |  | System | Error 1 Extra Info (MSB) |  |  |  |  | long
INPUT_REGISTER | Read | 4986 |  | System | Error 1 Extra Info (LSB) |  |  |  |  | long
INPUT_REGISTER | Read | 4988 |  | System | Error 2 Extra Info (MSB) |  |  |  |  | long
INPUT_REGISTER | Read | 4990 |  | System | Error 2 Extra Info (LSB) |  |  |  |  | long
INPUT_REGISTER | Read | 4992 |  | System | Error 3 Extra Info (MSB) |  |  |  |  | long
INPUT_REGISTER | Read | 4994 |  | System | Error 3 Extra Info (LSB) |  |  |  |  | long
INPUT_REGISTER | Read | 4996 |  | System | Error 4 Extra Info (MSB) |  |  |  |  | long
INPUT_REGISTER | Read | 4998 |  | System | Error 4 Extra Info (LSB) |  |  |  |  | long

## Slave10
Register Type | Permissions | Address | Bitblock Bit | Component | Name | Min | Max | Range | Unit | DataType | Float to Int Factor
HOLDING_REGISTER | Write | 5007 |  | DomesticHotWater Zm/Ems | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 5008 |  | DomesticHotWater Zm/Ems | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 5009 |  | DomesticHotWater Zm/Ems | Thermal Disinfection Setpoint | 65 | 75 |  | °C | int | x10
HOLDING_REGISTER | Write | 5010 |  | DomesticHotWater Zm | Setpoint Auto Day | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 5011 |  | DomesticHotWater Zm | Setpoint Auto Night | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 5012 |  | DomesticHotWater Zm | Setpoint Manual Day | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 5013 |  | DomesticHotWater Zm | Setpoint Manual Night | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 5014 |  | DomesticHotWater Zm | Setpoint Holiday | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 5015 |  | DomesticHotWater Zm/Ems | Circulation Pump Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 5016 |  | DomesticHotWater Zm/Ems | Circulation Pump Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 5017 |  | DomesticHotWater Zm/Ems | Disinfection Frequency | 0 | 7 | 0-Daily 1-Monday 2-Tuesday 3-Wednesday 4-Thursday 5-Friday 6-Saturday 7-Sunday |  | int
HOLDING_REGISTER | Write | 5018 |  | DomesticHotWater Zm/Ems | Disinfection Start Hour | 0 | 23 |  | h | int
HOLDING_REGISTER | Write | 5021 |  | DomesticHotWater Fm | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 5022 |  | DomesticHotWater Fm | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 5023 |  | DomesticHotWater Fm | Thermal Disinfection Setpoint | 65 | 75 |  | °C | int | x10
HOLDING_REGISTER | Write | 5024 |  | DomesticHotWater Fm | Setpoint Auto Day | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 5025 |  | DomesticHotWater Fm | Setpoint Auto Night | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 5026 |  | DomesticHotWater Fm | Setpoint Manual Day | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 5027 |  | DomesticHotWater Fm | Setpoint Manual Night | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 5028 |  | DomesticHotWater Fm | Setpoint Holiday | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 5029 |  | DomesticHotWater Fm | Circulation Pump Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 5030 |  | DomesticHotWater Fm | Circulation Pump Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 5031 |  | DomesticHotWater Fm | Disinfection Frequency | 0 | 7 | 0-Daily 1-Monday 2-Tuesday 3-Wednesday 4-Thursday 5-Friday 6-Saturday 7-Sunday |  | int
HOLDING_REGISTER | Write | 5032 |  | DomesticHotWater Fm | Disinfection Start Hour | 0 | 23 |  | h | int
HOLDING_REGISTER | Read | 5039 |  | Boiler | Control Type | 0 | 4 | 0-None 1-Safe 2-Ems 3-7Pole 4-Substation |  | int
HOLDING_REGISTER | Write | 5043 |  | AlternativeHeatSource | Operation Mode Request Auto Day | 20 | 99 |  | °C | int
HOLDING_REGISTER | Write | 5044 |  | AlternativeHeatSource | Operation Mode Request Auto Night | 20 | 99 |  | °C | int
HOLDING_REGISTER | Write | 5045 |  | AlternativeHeatSource | Operation Mode Request Manual Day | 20 | 99 |  | °C | int
HOLDING_REGISTER | Write | 5046 |  | AlternativeHeatSource | Operation Mode Request Manual Night | 20 | 99 |  | °C | int
HOLDING_REGISTER | Write | 5047 |  | AlternativeHeatSource | Operation Mode Request Holiday | 20 | 99 |  | °C | int
HOLDING_REGISTER | Write | 5048 |  | AlternativeHeatSource | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 5049 |  | AlternativeHeatSource | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 5050 |  | AlternativeHeatSource | Return Control Setpoint User | 10 | 70 |  | °C | int
HOLDING_REGISTER | Write | 5057 |  | HydraulicCircuit Zm | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 5058 |  | HydraulicCircuit Zm | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 5059 |  | HydraulicCircuit Zm | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5060 |  | HydraulicCircuit Zm | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5061 |  | HydraulicCircuit Zm | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5062 |  | HydraulicCircuit Zm | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5063 |  | HydraulicCircuit Zm | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5064 |  | HydraulicCircuit Zm | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 5070 |  | HydraulicCircuit 1 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 5071 |  | HydraulicCircuit 1 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 5072 |  | HydraulicCircuit 1 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5073 |  | HydraulicCircuit 1 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5074 |  | HydraulicCircuit 1 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5075 |  | HydraulicCircuit 1 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5076 |  | HydraulicCircuit 1 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5077 |  | HydraulicCircuit 1 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 5083 |  | HydraulicCircuit 2 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 5084 |  | HydraulicCircuit 2 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 5085 |  | HydraulicCircuit 2 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5086 |  | HydraulicCircuit 2 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5087 |  | HydraulicCircuit 2 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5088 |  | HydraulicCircuit 2 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5089 |  | HydraulicCircuit 2 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5090 |  | HydraulicCircuit 2 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 5096 |  | HydraulicCircuit 3 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 5097 |  | HydraulicCircuit 3 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 5098 |  | HydraulicCircuit 3 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5099 |  | HydraulicCircuit 3 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5100 |  | HydraulicCircuit 3 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5101 |  | HydraulicCircuit 3 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5102 |  | HydraulicCircuit 3 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5103 |  | HydraulicCircuit 3 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 5109 |  | HydraulicCircuit 4 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 5110 |  | HydraulicCircuit 4 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 5111 |  | HydraulicCircuit 4 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5112 |  | HydraulicCircuit 4 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5113 |  | HydraulicCircuit 4 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5114 |  | HydraulicCircuit 4 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5115 |  | HydraulicCircuit 4 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5116 |  | HydraulicCircuit 4 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 5122 |  | HydraulicCircuit 5 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 5123 |  | HydraulicCircuit 5 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 5124 |  | HydraulicCircuit 5 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5125 |  | HydraulicCircuit 5 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5126 |  | HydraulicCircuit 5 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5127 |  | HydraulicCircuit 5 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5128 |  | HydraulicCircuit 5 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5129 |  | HydraulicCircuit 5 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 5135 |  | HydraulicCircuit 6 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 5136 |  | HydraulicCircuit 6 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 5137 |  | HydraulicCircuit 6 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5138 |  | HydraulicCircuit 6 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5139 |  | HydraulicCircuit 6 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5140 |  | HydraulicCircuit 6 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5141 |  | HydraulicCircuit 6 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5142 |  | HydraulicCircuit 6 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 5148 |  | HydraulicCircuit 7 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 5149 |  | HydraulicCircuit 7 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 5150 |  | HydraulicCircuit 7 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5151 |  | HydraulicCircuit 7 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5152 |  | HydraulicCircuit 7 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5153 |  | HydraulicCircuit 7 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5154 |  | HydraulicCircuit 7 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5155 |  | HydraulicCircuit 7 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 5161 |  | HydraulicCircuit 8 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 5162 |  | HydraulicCircuit 8 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 5163 |  | HydraulicCircuit 8 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5164 |  | HydraulicCircuit 8 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5165 |  | HydraulicCircuit 8 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5166 |  | HydraulicCircuit 8 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5167 |  | HydraulicCircuit 8 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5168 |  | HydraulicCircuit 8 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 5201 |  | Heat Pump | Heat demand source | 0 | 2 | 0-Scheduler 1-System 2-Max_system_scheduler |  | int
HOLDING_REGISTER | Read | 5421 |  | Fresh Water Characteristics 3 | DHU Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 5422 |  | Fresh Water Characteristics 3 | Extra Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 5423 |  | Fresh Water Characteristics 3 | Maximum DHW Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 5424 |  | Fresh Water Characteristics 3 | On High Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 5425 |  | Fresh Water Characteristics 3 | On Low Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 5426 |  | Fresh Water Characteristics 3 | Fresh Water Type | 0 | 3 | 0-15/20l/min 1-27l/min 2-40l/min 3-60l/min |  | int
HOLDING_REGISTER | Read | 5427 |  | Fresh Water Characteristics 3 | Enable Alarm Output | 0 | 2 | 0-No 1-Yes 2-Inverted |  | int
HOLDING_REGISTER | Read | 5428 |  | Fresh Water Characteristics 3 | Buffer Cylinder Temperature Offset |  |  |  | K | int
HOLDING_REGISTER | Read | 5429 |  | Fresh Water Characteristics 3 | hrBitblock |  |  |  |  | int
| Read |  | 0 | Fresh Water | Buffer Cylinder Temperature Optimization Enabled |  |  |  |  | bit
| Read |  | 1 | Fresh Water | Impulse Enabled |  |  |  |  | bit
| Read |  | 2 | Fresh Water | Time Program Enabled |  |  |  |  | bit
HOLDING_REGISTER | Read | 5430 |  | Fresh Water Characteristics 3 | Minimum Buffer Cylinder Temperature Offset |  |  |  | K | int
HOLDING_REGISTER | Read | 5431 |  | Fresh Water Characteristics 2 | Circulation Pump Runs per Hour | 0 | 7 | 0-Undefined 1-1x3_minutes/h 2-2x3_minutes/h 3-3x3_minutes/h 4-4x3_minutes/h 5-5x3_minutes/h 6-6x3_minutes/h 7-Permanent |  | int
HOLDING_REGISTER | Read | 5432 |  | Fresh Water Characteristics 2 | Swich Hysteresis |  |  |  | K | int
HOLDING_REGISTER | Read | 5433 |  | Fresh Water Characteristics 2 | Thermal Disinfection Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 5434 |  | Fresh Water Characteristics 2 | Pre Heat Maximum Temperature |  |  |  | °C | int
INPUT_REGISTER | Read | 5000 |  | System | Own Outdoor temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5001 |  | System | Damped Own outdoor temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5004 |  | System | Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5008 |  | System | Active Functions 1 |  |  |  |  | int
INPUT_REGISTER | Read | 5009 |  | System | Active Functions 2 |  |  |  |  | int
INPUT_REGISTER | Read | 5015 |  | DomesticHotWater Zm | Charge Pump Running | 0 | 4 | 0-Stopping 1-Starting 2-Running 3-Off 4-Error |  | int
INPUT_REGISTER | Read | 5016 |  | DomesticHotWater Zm | Circulation Pump Running | 0 | 4 | 0-Stopping 1-Starting 2-Running 3-Off 4-Error |  | int
INPUT_REGISTER | Read | 5017 |  | DomesticHotWater Zm | Hydraulic State | 0 | 7 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Cold_load 6-Post_purge 7-Condense_protection |  | int
INPUT_REGISTER | Read | 5018 |  | DomesticHotWater Zm/Ems | Thermal Disinfection Status | 0 | 3 | 0-Off 1-On 2-Success 3-Error |  | int
INPUT_REGISTER | Read | 5019 |  | DomesticHotWater Zm/Ems | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 5020 |  | DomesticHotWater Zm/Ems | Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5021 |  | DomesticHotWater Zm/Ems | Current Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5031 |  | DomesticHotWater Fm | Charge Pump Running | 0 | 4 | 0-Stopping 1-Starting 2-Running 3-Off 4-Error |  | int
INPUT_REGISTER | Read | 5032 |  | DomesticHotWater Fm | Circulation Pump Running | 0 | 4 | 0-Stopping 1-Starting 2-Running 3-Off 4-Error |  | int
INPUT_REGISTER | Read | 5033 |  | DomesticHotWater Fm | Hydraulic State | 0 | 7 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Cold_load 6-Post_purge 7-Condense_protection |  | int
INPUT_REGISTER | Read | 5034 |  | DomesticHotWater Fm | Thermal Disinfection Status | 0 | 3 | 0-Off 1-On 2-Success 3-Error |  | int
INPUT_REGISTER | Read | 5035 |  | DomesticHotWater Fm | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 5036 |  | DomesticHotWater Fm | Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5037 |  | DomesticHotWater Fm | Current Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER |  | 5047 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 5048 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 5050 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 5052 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 5053 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 5054 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 5055 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 5056 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 5059 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 5060 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER | Read | 5063 |  | AlternativeHeatSource | Operating hours |  |  |  | h | long
INPUT_REGISTER | Read | 5065 |  | AlternativeHeatSource | Heat Source Starts |  |  |  |  | long
INPUT_REGISTER | Read | 5067 |  | AlternativeHeatSource | Heat Source Hours to Maintenance |  |  |  | h | int
INPUT_REGISTER | Read | 5069 |  | AlternativeHeatSource | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
| Read |  | 0 | AlternativeHeatSource | Is Heat Source On |  |  |  |  | bit
| Read |  | 1 | AlternativeHeatSource | Is Heat Source On Request |  |  |  |  | bit
INPUT_REGISTER | Read | 5087 |  | HydraulicCircuit Zm | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5088 |  | HydraulicCircuit Zm | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5089 |  | HydraulicCircuit Zm | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5090 |  | HydraulicCircuit Zm | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5091 |  | HydraulicCircuit Zm | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 5092 |  | HydraulicCircuit Zm | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 5093 |  | HydraulicCircuit Zm | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 5094 |  | HydraulicCircuit Zm | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 5095 |  | HydraulicCircuit Zm | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 5099 |  | HydraulicCircuit 1 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5100 |  | HydraulicCircuit 1 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5101 |  | HydraulicCircuit 1 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5102 |  | HydraulicCircuit 1 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5103 |  | HydraulicCircuit 1 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 5104 |  | HydraulicCircuit 1 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 5105 |  | HydraulicCircuit 1 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 5106 |  | HydraulicCircuit 1 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 5107 |  | HydraulicCircuit 1 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 5112 |  | HydraulicCircuit 2 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5113 |  | HydraulicCircuit 2 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5114 |  | HydraulicCircuit 2 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5115 |  | HydraulicCircuit 2 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5116 |  | HydraulicCircuit 2 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 5117 |  | HydraulicCircuit 2 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 5118 |  | HydraulicCircuit 2 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 5119 |  | HydraulicCircuit 2 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 5120 |  | HydraulicCircuit 2 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 5125 |  | HydraulicCircuit 3 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5126 |  | HydraulicCircuit 3 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5127 |  | HydraulicCircuit 3 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5128 |  | HydraulicCircuit 3 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5129 |  | HydraulicCircuit 3 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 5130 |  | HydraulicCircuit 3 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 5131 |  | HydraulicCircuit 3 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 5132 |  | HydraulicCircuit 3 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 5133 |  | HydraulicCircuit 3 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 5138 |  | HydraulicCircuit 4 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5139 |  | HydraulicCircuit 4 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5140 |  | HydraulicCircuit 4 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5141 |  | HydraulicCircuit 4 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5142 |  | HydraulicCircuit 4 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 5143 |  | HydraulicCircuit 4 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 5144 |  | HydraulicCircuit 4 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 5145 |  | HydraulicCircuit 4 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 5146 |  | HydraulicCircuit 4 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 5151 |  | HydraulicCircuit 5 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5152 |  | HydraulicCircuit 5 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5153 |  | HydraulicCircuit 5 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5154 |  | HydraulicCircuit 5 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5155 |  | HydraulicCircuit 5 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 5156 |  | HydraulicCircuit 5 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 5157 |  | HydraulicCircuit 5 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 5158 |  | HydraulicCircuit 5 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 5159 |  | HydraulicCircuit 5 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 5164 |  | HydraulicCircuit 6 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5165 |  | HydraulicCircuit 6 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5166 |  | HydraulicCircuit 6 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5167 |  | HydraulicCircuit 6 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5168 |  | HydraulicCircuit 6 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 5169 |  | HydraulicCircuit 6 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 5170 |  | HydraulicCircuit 6 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 5171 |  | HydraulicCircuit 6 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 5172 |  | HydraulicCircuit 6 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 5177 |  | HydraulicCircuit 7 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5178 |  | HydraulicCircuit 7 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5179 |  | HydraulicCircuit 7 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5180 |  | HydraulicCircuit 7 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5181 |  | HydraulicCircuit 7 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 5182 |  | HydraulicCircuit 7 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 5183 |  | HydraulicCircuit 7 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 5184 |  | HydraulicCircuit 7 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 5185 |  | HydraulicCircuit 7 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 5190 |  | HydraulicCircuit 8 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5191 |  | HydraulicCircuit 8 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5192 |  | HydraulicCircuit 8 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5193 |  | HydraulicCircuit 8 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5194 |  | HydraulicCircuit 8 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 5195 |  | HydraulicCircuit 8 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 5196 |  | HydraulicCircuit 8 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 5197 |  | HydraulicCircuit 8 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 5198 |  | HydraulicCircuit 8 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 5203 |  | i2c | Global Error State | 0 | 4 | 0-No_Error 1-i2c_driver_error 2-Wrong_Cycle_Time 3-Missing_Module_Slot 4-Module_Slot_Error |  | int
INPUT_REGISTER | Read | 5204 |  | i2c | Slot1 Module Detected |  |  | 0-Unknown 1-None 22-FM_CM 25-FM_SI 28-FM_MM 29-FM_MW 30-FM_AM 31-FM_CM2 |  | int
INPUT_REGISTER | Read | 5205 |  | i2c | Slot1 Error State |  |  | 0-No_Error 1-No_Response 2-Wrong_Module 3-Unsupported_Module 4-Internal_Sw_Error 5-Communication_Failed 6-Internal_Module_Error 7-Module_Not_Supported_Current_Variant 8-Module_Not_Suppported_In_Slot 9-Module_Count_Too_High 10-Module_Not_Supported_With_Connected_Boiler_Type |  | int
INPUT_REGISTER | Read | 5206 |  | i2c | Slot2 Module Detected |  |  | 0-Unknown 1-None 22-FM_CM 25-FM_SI 28-FM_MM 29-FM_MW 30-FM_AM 31-FM_CM2 |  | int
INPUT_REGISTER | Read | 5207 |  | i2c | Slot2 Error State |  |  | 0-No_Error 1-No_Response 2-Wrong_Module 3-Unsupported_Module 4-Internal_Sw_Error 5-Communication_Failed 6-Internal_Module_Error 7-Module_Not_Supported_Current_Variant 8-Module_Not_Suppported_In_Slot 9-Module_Count_Too_High 10-Module_Not_Supported_With_Connected_Boiler_Type |  | int
INPUT_REGISTER | Read | 5208 |  | i2c | Slot3 Module Detected |  |  | 0-Unknown 1-None 22-FM_CM 25-FM_SI 28-FM_MM 29-FM_MW 30-FM_AM 31-FM_CM2 |  | int
INPUT_REGISTER | Read | 5209 |  | i2c | Slot3 Error State |  |  | 0-No_Error 1-No_Response 2-Wrong_Module 3-Unsupported_Module 4-Internal_Sw_Error 5-Communication_Failed 6-Internal_Module_Error 7-Module_Not_Supported_Current_Variant 8-Module_Not_Suppported_In_Slot 9-Module_Count_Too_High 10-Module_Not_Supported_With_Connected_Boiler_Type |  | int
INPUT_REGISTER | Read | 5210 |  | i2c | Slot4 Module Detected |  |  | 0-Unknown 1-None 22-FM_CM 25-FM_SI 28-FM_MM 29-FM_MW 30-FM_AM 31-FM_CM2 |  | int
INPUT_REGISTER | Read | 5211 |  | i2c | Slot4 Error State |  |  | 0-No_Error 1-No_Response 2-Wrong_Module 3-Unsupported_Module 4-Internal_Sw_Error 5-Communication_Failed 6-Internal_Module_Error 7-Module_Not_Supported_Current_Variant 8-Module_Not_Suppported_In_Slot 9-Module_Count_Too_High 10-Module_Not_Supported_With_Connected_Boiler_Type |  | int
INPUT_REGISTER | Read | 5212 |  | i2c | Slot A Module Detected |  |  | 0-Unknown 1-None 26-ZM5313 27-ZM5311 |  | int
INPUT_REGISTER | Read | 5213 |  | i2c | Slot A Error State |  |  | 0-No_Error 1-No_Response 2-Wrong_Module 3-Unsupported_Module 4-Internal_Sw_Error 5-Communication_Failed 6-Internal_Module_Error 7-Module_Not_Supported_Current_Variant 8-Module_Not_Suppported_In_Slot 9-Module_Count_Too_High 10-Module_Not_Supported_With_Connected_Boiler_Type |  | int
INPUT_REGISTER | Read | 5214 |  | i2c | irBitblock |  |  |  |  | int
| Read |  | 0 | i2c | Component Error |  |  |  |  | bit
INPUT_REGISTER | Read | 5225 |  | fm-si | irBitblock |  |  |  |  | int
| Read |  | 0 | fm-si | Input 1 Error |  |  |  |  | bit
| Read |  | 1 | fm-si | Input 2 Error |  |  |  |  | bit
| Read |  | 2 | fm-si | Input 3 Error |  |  |  |  | bit
| Read |  | 3 | fm-si | Input 4 Error |  |  |  |  | bit
| Read |  | 4 | fm-si | Input 5 Error |  |  |  |  | bit
INPUT_REGISTER | Read | 5232 |  | Sdc | Demand Mode (Low Priority) | 0 | 2 | 0-Off 1-Take_Heat 2-Give_Heat |  | int
INPUT_REGISTER | Read | 5233 |  | Sdc | Demand Flow Temp (Low Priority) |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5234 |  | Sdc | Demand Mode (High Priority) | 0 | 2 | 0-Off 1-Take_Heat 2-Give_Heat |  | int
INPUT_REGISTER | Read | 5235 |  | Sdc | Demand Flow Temp (High Priority) |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5239 |  | Heat Pump | System return temperature for HP heating buffer |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5240 |  | Heat Pump | Buffer mid temperature for HP heating buffer |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5241 |  | Heat Pump | Buffer top temperature for HP heating buffer |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5242 |  | Heat Pump | Buffer bottom temperature for HP heating buffer |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5243 |  | Heat Pump | Return temperature FWR |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5244 |  | Heat Pump | Flow temperature FWV |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5245 |  | Heat Pump | Flow temperature HP |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5246 |  | Heat Pump | Return temperature HP |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5247 |  | Heat Pump | HMI State of HP Component | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 5248 |  | Heat Pump | HP current heat output |  |  |  | kW | signed int | x10
INPUT_REGISTER | Read | 5249 |  | Heat Pump | HP current electrical power consumption | 0 | 10000 |  | kW | int | x10
INPUT_REGISTER | Read | 5250 |  | Heat Pump | HP Smart grid mode | 0 | 3 | 0-normal_charging_grid 1-low_charging_grid 2-high_charging_grid 3-free_charging_grid |  | int
INPUT_REGISTER | Read | 5251 |  | Heat Pump | Heat demand temperature set point |  |  |  | °C | int
INPUT_REGISTER | Read | 5252 |  | Heat Pump | heatPumpStatusIrBitblock | 0 |  |  |  | int
INPUT_REGISTER | Read | 5253 |  | Heat Pump | Ambient Temperature HP |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5254 |  | Heat Pump | HP silent mode | 0 | 3 | 0-standard_mode 1-silent_mode 2-super_silent_mode 3-night_mode |  | int
INPUT_REGISTER | Read | 5255 |  | Heat Pump | Heat Pump Heat Request Temperature |  |  |  | °C | int
INPUT_REGISTER | Read | 5256 |  | Heat Pump | heatPumpIrBitblock |  |  |  |  | int
INPUT_REGISTER | Read | 5265 |  | System | Open Notifications Count |  |  |  |  | int
INPUT_REGISTER | Read | 5266 |  | System | Error Key 5 |  |  |  |  | long
INPUT_REGISTER | Read | 5268 |  | System | Error Key 6 |  |  |  |  | long
INPUT_REGISTER | Read | 5270 |  | System | Error Key 7 |  |  |  |  | long
INPUT_REGISTER | Read | 5272 |  | System | Error Key 8 |  |  |  |  | long
INPUT_REGISTER | Read | 5274 |  | System | Error Key 9 |  |  |  |  | long
INPUT_REGISTER | Read | 5276 |  | System | Error Key 10 |  |  |  |  | long
INPUT_REGISTER | Read | 5278 |  | Chp / EC Power | Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5279 |  | Chp / EC Power | Return Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5280 |  | Chp | Flue Gas Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5281 |  | Chp | Motor Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5282 |  | Chp / EC Power | Current Generator Power |  |  |  | kW | int
INPUT_REGISTER | Read | 5283 |  | Chp | Current Power Setpoint |  |  |  | kW | int
INPUT_REGISTER | Read | 5284 |  | Chp / EC Power | Operation Hours |  |  |  | h | long
INPUT_REGISTER | Read | 5286 |  | Chp / EC Power | Number of starts |  |  |  |  | long
INPUT_REGISTER | Read | 5288 |  | Chp / EC Power | Hours to Maintenance |  |  |  | h | int
INPUT_REGISTER | Read | 5290 |  | Chp | Output Power Setpoint |  |  |  | kW | int
INPUT_REGISTER | Read | 5291 |  | Chp | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 5296 |  | Chp | irBitblock |  |  |  |  | int
| Read |  | 0 | Chp | Warning |  |  |  |  | bit
| Read |  | 1 | Chp / EC Power | Malfunction |  |  |  |  | bit
| Read |  | 2 | Chp / EC Power | Controlled Shutdown |  |  |  |  | bit
| Read |  | 3 | Chp / EC Power | Generator On |  |  |  |  | bit
| Read |  | 4 | Chp | Automatic On |  |  |  |  | bit
| Read |  | 5 | Chp / EC Power | Automatic Ready |  |  |  |  | bit
| Read |  | 11 | Chp / EC Power | Output On Request |  |  |  |  | bit
INPUT_REGISTER | Read | 5304 |  | Water Treatment Module | Program Step |  |  | 20-140: Desalination not active 10000-10810: One time desalination 20000-20810: Automatic desalination 30000-30260: Stationary operation |  | int
INPUT_REGISTER | Read | 5305 |  | Water Treatment Module | Temperature Desalinization |  |  |  | °C | int | x10
INPUT_REGISTER | Read | 5306 |  | Water Treatment Module | Volume Flow |  |  |  | L/min | int | x10
INPUT_REGISTER | Read | 5307 |  | Water Treatment Module | Conductivity system |  |  |  | uS/cm | int | x10
INPUT_REGISTER | Read | 5308 |  | Water Treatment Module | Conductivity cartridge |  |  |  | uS/cm | int | x10
INPUT_REGISTER | Read | 5309 |  | Water Treatment Module | Cartridge Capacity |  |  |  | % | int
INPUT_REGISTER | Read | 5313 |  | Solar Data | Collector temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5314 |  | Solar Data | Temperature cylinder bottom |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5315 |  | Solar Data | Solar pump modulation setpoint |  |  |  | % | int
INPUT_REGISTER | Read | 5316 |  | Solar | Solar pump status | 0 | 19 | 1-TestMod 2-BlckProt 3-No heat 4-Ht avail 5-SolOff 6-MaxCyl 7-MaxColl 8-MinColl 9-FrostP 10-VacFct 11-SwChck 12-MixPrio 13-Switch 14-Priority 15-ThermD 16-MixCal 17-MixOpn 18-MixCl 19-MixOff |  | int
INPUT_REGISTER | Read | 5317 |  | Solar Data | Heat exchanger temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5318 |  | Solar Data | Heat exchanger pump modulation setpoint |  |  |  | % | int
INPUT_REGISTER | Read | 5319 |  | Solar | Heat exchanger pump status | 0 | 19 | 1-TestMod 2-BlckProt 3-No heat 4-Ht avail 5-SolOff 6-MaxCyl 7-MaxColl 8-MinColl 9-FrostP 10-VacFct 11-SwChck 12-MixPrio 13-Switch 14-Priority 15-ThermD 16-MixCal 17-MixOpn 18-MixCl 19-MixOff |  | int
INPUT_REGISTER | Read | 5320 |  | Solar Data | Temperature cylinder 3 top |  |  |  | °C | int | x10
INPUT_REGISTER | Read | 5321 |  | Solar Data | Reload pump modulation setpoint |  |  |  | % | int
INPUT_REGISTER | Read | 5322 |  | Solar | Reload pump status | 0 | 19 | 1-TestMod 2-BlckProt 3-No heat 4-Ht avail 5-SolOff 6-MaxCyl 7-MaxColl 8-MinColl 9-FrostP 10-VacFct 11-SwChck 12-MixPrio 13-Switch 14-Priority 15-ThermD 16-MixCal 17-MixOpn 18-MixCl 19-MixOff |  | int
INPUT_REGISTER | Read | 5323 |  | Solar | Pump therm. disinfect. status | 0 | 19 | 1-TestMod 2-BlckProt 3-No heat 4-Ht avail 5-SolOff 6-MaxCyl 7-MaxColl 8-MinColl 9-FrostP 10-VacFct 11-SwChck 12-MixPrio 13-Switch 14-Priority 15-ThermD 16-MixCal 17-MixOpn 18-MixCl 19-MixOff |  | int
INPUT_REGISTER | Read | 5324 |  | Solar Yield | Flow temperature heat meter |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5325 |  | Solar Yield | Return temperature heat meter |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5326 |  | Solar Yield | Heat count pulse counter | 0 | 15 |  |  | int
INPUT_REGISTER | Read | 5327 |  | Solar Yield | Solar yield per month |  |  |  | kWh | long | x10
INPUT_REGISTER | Read | 5329 |  | Solar Yield | Solar yield per year |  |  |  | kWh | long | x10
INPUT_REGISTER | Read | 5331 |  | Solar Yield | Last hour solar yield |  |  |  | kWh | long | x10
INPUT_REGISTER | Read | 5333 |  | Solar Yield | Solar yield per day |  |  |  | kWh | long | x10
INPUT_REGISTER | Read | 5335 |  | Solar Yield | Solar yield since installation |  |  |  | kWh | long | x10
INPUT_REGISTER | Read | 5337 |  | Solar | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 5338 |  | Solar Data | Hydraulic configuration |  |  |  |  | int
| Read |  | 0 | Solar | Option 1 active |  |  |  |  | bit
| Read |  | 1 | Solar | Option A active |  |  |  |  | bit
| Read |  | 2 | Solar | Option B active |  |  |  |  | bit
| Read |  | 3 | Solar | Option C active |  |  |  |  | bit
| Read |  | 4 | Solar | Option D active |  |  |  |  | bit
| Read |  | 5 | Solar | Option E active |  |  |  |  | bit
| Read |  | 6 | Solar | Option F active |  |  |  |  | bit
| Read |  | 7 | Solar | Option G active |  |  |  |  | bit
| Read |  | 8 | Solar | Option H active |  |  |  |  | bit
| Read |  | 9 | Solar | Option I active |  |  |  |  | bit
| Read |  | 10 | Solar | Option J active |  |  |  |  | bit
| Read |  | 11 | Solar | Option K active |  |  |  |  | bit
| Read |  | 12 | Solar | Option L active |  |  |  |  | bit
| Read |  | 13 | Solar | Option M active |  |  |  |  | bit
| Read |  | 14 | Solar | Option N active |  |  |  |  | bit
| Read |  | 15 | Solar | Option P active |  |  |  |  | bit
INPUT_REGISTER | Read | 5339 |  | Solar Data | irBitblock |  |  |  |  | int
| Read |  | 0 | Solar | Is Active |  |  |  |  | bit
INPUT_REGISTER |  | 5400 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 5401 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 5402 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 5403 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 5404 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 5405 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 5406 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 5407 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 5408 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 5409 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 5410 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 5411 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 5412 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 5413 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER | Read | 5422 |  | Energy Monitoring | Heat Output |  |  |  | kW | signed int | x10
INPUT_REGISTER | Read | 5423 |  | Energy Monitoring | Gas Consumption (LCV) |  |  |  | kW | signed int | x10
INPUT_REGISTER | Read | 5425 |  | Energy Monitoring | Electrical Power |  |  |  | W | int
INPUT_REGISTER | Read | 5430 |  | Fresh Water Characteristics 1 | DHW Out Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5431 |  | Fresh Water Characteristics 1 | DHW Volume Flow |  |  |  | L/min | signed int | x10
INPUT_REGISTER | Read | 5432 |  | Fresh Water Characteristics 1 | Prim In Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5433 |  | Fresh Water Characteristics 1 | DHW In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5434 |  | Fresh Water Characteristics 1 | Primary Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 5435 |  | Fresh Water Characteristics 1 | Request DHW Out Temperature |  |  |  | °C | int
INPUT_REGISTER | Read | 5436 |  | Fresh Water Characteristics 1 | Status Request DHW Out Temperature | 0 | 9 | 0-Off 1-DHWRed 2-DHW 3-Sol_red 4-Once_on 5-Therm_d 6-DlyHtUp 7-Preheat_start 8-Preheat_normal 9-No_eq |  | int
INPUT_REGISTER | Read | 5437 |  | Fresh Water Characteristics 2 | Circulation Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 5438 |  | Fresh Water Characteristics 2 | Status Circulation Pump | 0 | 8 | 0-Undefined 1-Test 2-BlckProt 3-No_req 4-AutoOff 5-AutoOn 6-Therm_d 7-Sys_Off 8-DlyHtUp |  | int
INPUT_REGISTER | Read | 5439 |  | Fresh Water Characteristics 2 | Return Valve Modulation Request |  |  |  | % | int
INPUT_REGISTER | Read | 5440 |  | Fresh Water Characteristics 2 | Valve State | 0 | 5 | 0-Undefined 1-TestMod 2-BlckProt 3-Mix_cl 4-Mix_opn 5-Sys_Off |  | int
INPUT_REGISTER | Read | 5441 |  | Fresh Water Characteristics 2 | Return Valve Buffer Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5442 |  | Fresh Water Characteristics 2 | Disinfection Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 5443 |  | Fresh Water Characteristics 2 | Pump State | 0 | 5 | 0-Undefined 1-TestMod 2-BlckPro 3-No_eq 4-Ht_req 5-Sys_Off |  | int
INPUT_REGISTER | Read | 5444 |  | Fresh Water Characteristics 1 | DHW Valve Power |  |  |  | % | int
INPUT_REGISTER | Read | 5445 |  | Fresh Water Characteristics 2 | Total Flow |  |  |  | L/min | int | x10
INPUT_REGISTER | Read | 5446 |  | Fresh Water 2 | Module 2 DHW Out Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5447 |  | Fresh Water 2 | Module 2 DHW Volume Flow |  |  |  | L/min | signed int | x10
INPUT_REGISTER | Read | 5448 |  | Fresh Water 2 | Module 2 Prim In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5449 |  | Fresh Water 2 | Module 2 DHW In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5450 |  | Fresh Water 2 | Module 2 DHW Valve Power |  |  |  | % | int
INPUT_REGISTER | Read | 5451 |  | Fresh Water 2 | Module 2 Prim Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 5452 |  | Fresh Water 2 | Module 2 Status Prim Pump |  |  |  |  | int
INPUT_REGISTER | Read | 5453 |  | Fresh Water 3 | Module 3 DHW Out Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5454 |  | Fresh Water 3 | Module 3 DHW Volume Flow |  |  |  | L/min | signed int | x10
INPUT_REGISTER | Read | 5455 |  | Fresh Water 3 | Module 3 Prim In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5456 |  | Fresh Water 3 | Module 3 DHW In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5457 |  | Fresh Water 3 | Module 3 DHW Valve Power |  |  |  | % | int
INPUT_REGISTER | Read | 5458 |  | Fresh Water 3 | Module 3 Prim Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 5459 |  | Fresh Water 3 | Module 3 Status Prim Pump |  |  |  |  | int
INPUT_REGISTER | Read | 5460 |  | Fresh Water 4 | Module 4 DHW Out Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5461 |  | Fresh Water 4 | Module 4 DHW Volume Flow |  |  |  | L/min | signed int | x10
INPUT_REGISTER | Read | 5462 |  | Fresh Water 4 | Module 4 Prim In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5463 |  | Fresh Water 4 | Module 4 DHW In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5464 |  | Fresh Water 4 | Module 4 DHW ValvePower |  |  |  | % | int
INPUT_REGISTER | Read | 5465 |  | Fresh Water 4 | Module 4 Prim Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 5466 |  | Fresh Water 4 | Module 4 Status Primary Pump |  |  |  |  | int
INPUT_REGISTER | Read | 5467 |  | Fresh Water | Fresh Water Hmi State |  |  |  |  | int
INPUT_REGISTER | Read | 5468 |  | Fresh Water Characteristics 3 | Fresh Water Configurations |  |  |  |  | int
| Read |  | 0 | Fresh Water | Option 2 active |  |  |  |  | bit
| Read |  | 1 | Fresh Water | Option A active |  |  |  |  | bit
| Read |  | 2 | Fresh Water | Option B active |  |  |  |  | bit
| Read |  | 3 | Fresh Water | Option C active |  |  |  |  | bit
| Read |  | 4 | Fresh Water | Option D active |  |  |  |  | bit
| Read |  | 5 | Fresh Water | Option E active |  |  |  |  | bit
| Read |  | 6 | Fresh Water | Option E active cascade module 2 active |  |  |  |  | bit
| Read |  | 7 | Fresh Water | Option E active cascade module 3 active |  |  |  |  | bit
| Read |  | 8 | Fresh Water | Option E active cascade module 4 active |  |  |  |  | bit
| Read |  | 9 | Fresh Water | Is Active |  |  |  |  | bit
INPUT_REGISTER | Read | 5476 |  | System | Error Key 1 |  |  |  |  | long
INPUT_REGISTER | Read | 5478 |  | System | Error Key 2 |  |  |  |  | long
INPUT_REGISTER | Read | 5480 |  | System | Error Key 3 |  |  |  |  | long
INPUT_REGISTER | Read | 5482 |  | System | Error Key 4 |  |  |  |  | long
INPUT_REGISTER | Read | 5484 |  | System | Error 1 Extra Info (MSB) |  |  |  |  | long
INPUT_REGISTER | Read | 5486 |  | System | Error 1 Extra Info (LSB) |  |  |  |  | long
INPUT_REGISTER | Read | 5488 |  | System | Error 2 Extra Info (MSB) |  |  |  |  | long
INPUT_REGISTER | Read | 5490 |  | System | Error 2 Extra Info (LSB) |  |  |  |  | long
INPUT_REGISTER | Read | 5492 |  | System | Error 3 Extra Info (MSB) |  |  |  |  | long
INPUT_REGISTER | Read | 5494 |  | System | Error 3 Extra Info (LSB) |  |  |  |  | long
INPUT_REGISTER | Read | 5496 |  | System | Error 4 Extra Info (MSB) |  |  |  |  | long
INPUT_REGISTER | Read | 5498 |  | System | Error 4 Extra Info (LSB) |  |  |  |  | long

## Slave11
Register Type | Permissions | Address | Bitblock Bit | Component | Name | Min | Max | Range | Unit | DataType | Float to Int Factor
HOLDING_REGISTER | Write | 5507 |  | DomesticHotWater Zm/Ems | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 5508 |  | DomesticHotWater Zm/Ems | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 5509 |  | DomesticHotWater Zm/Ems | Thermal Disinfection Setpoint | 65 | 75 |  | °C | int | x10
HOLDING_REGISTER | Write | 5510 |  | DomesticHotWater Zm | Setpoint Auto Day | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 5511 |  | DomesticHotWater Zm | Setpoint Auto Night | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 5512 |  | DomesticHotWater Zm | Setpoint Manual Day | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 5513 |  | DomesticHotWater Zm | Setpoint Manual Night | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 5514 |  | DomesticHotWater Zm | Setpoint Holiday | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 5515 |  | DomesticHotWater Zm/Ems | Circulation Pump Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 5516 |  | DomesticHotWater Zm/Ems | Circulation Pump Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 5517 |  | DomesticHotWater Zm/Ems | Disinfection Frequency | 0 | 7 | 0-Daily 1-Monday 2-Tuesday 3-Wednesday 4-Thursday 5-Friday 6-Saturday 7-Sunday |  | int
HOLDING_REGISTER | Write | 5518 |  | DomesticHotWater Zm/Ems | Disinfection Start Hour | 0 | 23 |  | h | int
HOLDING_REGISTER | Write | 5521 |  | DomesticHotWater Fm | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 5522 |  | DomesticHotWater Fm | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 5523 |  | DomesticHotWater Fm | Thermal Disinfection Setpoint | 65 | 75 |  | °C | int | x10
HOLDING_REGISTER | Write | 5524 |  | DomesticHotWater Fm | Setpoint Auto Day | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 5525 |  | DomesticHotWater Fm | Setpoint Auto Night | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 5526 |  | DomesticHotWater Fm | Setpoint Manual Day | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 5527 |  | DomesticHotWater Fm | Setpoint Manual Night | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 5528 |  | DomesticHotWater Fm | Setpoint Holiday | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 5529 |  | DomesticHotWater Fm | Circulation Pump Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 5530 |  | DomesticHotWater Fm | Circulation Pump Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 5531 |  | DomesticHotWater Fm | Disinfection Frequency | 0 | 7 | 0-Daily 1-Monday 2-Tuesday 3-Wednesday 4-Thursday 5-Friday 6-Saturday 7-Sunday |  | int
HOLDING_REGISTER | Write | 5532 |  | DomesticHotWater Fm | Disinfection Start Hour | 0 | 23 |  | h | int
HOLDING_REGISTER | Read | 5539 |  | Boiler | Control Type | 0 | 4 | 0-None 1-Safe 2-Ems 3-7Pole 4-Substation |  | int
HOLDING_REGISTER | Write | 5543 |  | AlternativeHeatSource | Operation Mode Request Auto Day | 20 | 99 |  | °C | int
HOLDING_REGISTER | Write | 5544 |  | AlternativeHeatSource | Operation Mode Request Auto Night | 20 | 99 |  | °C | int
HOLDING_REGISTER | Write | 5545 |  | AlternativeHeatSource | Operation Mode Request Manual Day | 20 | 99 |  | °C | int
HOLDING_REGISTER | Write | 5546 |  | AlternativeHeatSource | Operation Mode Request Manual Night | 20 | 99 |  | °C | int
HOLDING_REGISTER | Write | 5547 |  | AlternativeHeatSource | Operation Mode Request Holiday | 20 | 99 |  | °C | int
HOLDING_REGISTER | Write | 5548 |  | AlternativeHeatSource | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 5549 |  | AlternativeHeatSource | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 5550 |  | AlternativeHeatSource | Return Control Setpoint User | 10 | 70 |  | °C | int
HOLDING_REGISTER | Write | 5557 |  | HydraulicCircuit Zm | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 5558 |  | HydraulicCircuit Zm | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 5559 |  | HydraulicCircuit Zm | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5560 |  | HydraulicCircuit Zm | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5561 |  | HydraulicCircuit Zm | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5562 |  | HydraulicCircuit Zm | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5563 |  | HydraulicCircuit Zm | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5564 |  | HydraulicCircuit Zm | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 5570 |  | HydraulicCircuit 1 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 5571 |  | HydraulicCircuit 1 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 5572 |  | HydraulicCircuit 1 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5573 |  | HydraulicCircuit 1 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5574 |  | HydraulicCircuit 1 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5575 |  | HydraulicCircuit 1 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5576 |  | HydraulicCircuit 1 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5577 |  | HydraulicCircuit 1 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 5583 |  | HydraulicCircuit 2 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 5584 |  | HydraulicCircuit 2 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 5585 |  | HydraulicCircuit 2 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5586 |  | HydraulicCircuit 2 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5587 |  | HydraulicCircuit 2 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5588 |  | HydraulicCircuit 2 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5589 |  | HydraulicCircuit 2 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5590 |  | HydraulicCircuit 2 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 5596 |  | HydraulicCircuit 3 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 5597 |  | HydraulicCircuit 3 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 5598 |  | HydraulicCircuit 3 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5599 |  | HydraulicCircuit 3 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5600 |  | HydraulicCircuit 3 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5601 |  | HydraulicCircuit 3 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5602 |  | HydraulicCircuit 3 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5603 |  | HydraulicCircuit 3 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 5609 |  | HydraulicCircuit 4 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 5610 |  | HydraulicCircuit 4 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 5611 |  | HydraulicCircuit 4 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5612 |  | HydraulicCircuit 4 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5613 |  | HydraulicCircuit 4 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5614 |  | HydraulicCircuit 4 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5615 |  | HydraulicCircuit 4 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5616 |  | HydraulicCircuit 4 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 5622 |  | HydraulicCircuit 5 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 5623 |  | HydraulicCircuit 5 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 5624 |  | HydraulicCircuit 5 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5625 |  | HydraulicCircuit 5 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5626 |  | HydraulicCircuit 5 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5627 |  | HydraulicCircuit 5 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5628 |  | HydraulicCircuit 5 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5629 |  | HydraulicCircuit 5 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 5635 |  | HydraulicCircuit 6 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 5636 |  | HydraulicCircuit 6 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 5637 |  | HydraulicCircuit 6 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5638 |  | HydraulicCircuit 6 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5639 |  | HydraulicCircuit 6 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5640 |  | HydraulicCircuit 6 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5641 |  | HydraulicCircuit 6 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5642 |  | HydraulicCircuit 6 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 5648 |  | HydraulicCircuit 7 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 5649 |  | HydraulicCircuit 7 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 5650 |  | HydraulicCircuit 7 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5651 |  | HydraulicCircuit 7 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5652 |  | HydraulicCircuit 7 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5653 |  | HydraulicCircuit 7 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5654 |  | HydraulicCircuit 7 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5655 |  | HydraulicCircuit 7 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 5661 |  | HydraulicCircuit 8 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 5662 |  | HydraulicCircuit 8 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 5663 |  | HydraulicCircuit 8 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5664 |  | HydraulicCircuit 8 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5665 |  | HydraulicCircuit 8 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5666 |  | HydraulicCircuit 8 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5667 |  | HydraulicCircuit 8 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 5668 |  | HydraulicCircuit 8 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 5701 |  | Heat Pump | Heat demand source | 0 | 2 | 0-Scheduler 1-System 2-Max_system_scheduler |  | int
HOLDING_REGISTER | Read | 5921 |  | Fresh Water Characteristics 3 | DHU Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 5922 |  | Fresh Water Characteristics 3 | Extra Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 5923 |  | Fresh Water Characteristics 3 | Maximum DHW Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 5924 |  | Fresh Water Characteristics 3 | On High Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 5925 |  | Fresh Water Characteristics 3 | On Low Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 5926 |  | Fresh Water Characteristics 3 | Fresh Water Type | 0 | 3 | 0-15/20l/min 1-27l/min 2-40l/min 3-60l/min |  | int
HOLDING_REGISTER | Read | 5927 |  | Fresh Water Characteristics 3 | Enable Alarm Output | 0 | 2 | 0-No 1-Yes 2-Inverted |  | int
HOLDING_REGISTER | Read | 5928 |  | Fresh Water Characteristics 3 | Buffer Cylinder Temperature Offset |  |  |  | K | int
HOLDING_REGISTER | Read | 5929 |  | Fresh Water Characteristics 3 | hrBitblock |  |  |  |  | int
| Read |  | 0 | Fresh Water | Buffer Cylinder Temperature Optimization Enabled |  |  |  |  | bit
| Read |  | 1 | Fresh Water | Impulse Enabled |  |  |  |  | bit
| Read |  | 2 | Fresh Water | Time Program Enabled |  |  |  |  | bit
HOLDING_REGISTER | Read | 5930 |  | Fresh Water Characteristics 3 | Minimum Buffer Cylinder Temperature Offset |  |  |  | K | int
HOLDING_REGISTER | Read | 5931 |  | Fresh Water Characteristics 2 | Circulation Pump Runs per Hour | 0 | 7 | 0-Undefined 1-1x3_minutes/h 2-2x3_minutes/h 3-3x3_minutes/h 4-4x3_minutes/h 5-5x3_minutes/h 6-6x3_minutes/h 7-Permanent |  | int
HOLDING_REGISTER | Read | 5932 |  | Fresh Water Characteristics 2 | Swich Hysteresis |  |  |  | K | int
HOLDING_REGISTER | Read | 5933 |  | Fresh Water Characteristics 2 | Thermal Disinfection Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 5934 |  | Fresh Water Characteristics 2 | Pre Heat Maximum Temperature |  |  |  | °C | int
INPUT_REGISTER | Read | 5500 |  | System | Own Outdoor temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5501 |  | System | Damped Own outdoor temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5504 |  | System | Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5508 |  | System | Active Functions 1 |  |  |  |  | int
INPUT_REGISTER | Read | 5509 |  | System | Active Functions 2 |  |  |  |  | int
INPUT_REGISTER | Read | 5515 |  | DomesticHotWater Zm | Charge Pump Running | 0 | 4 | 0-Stopping 1-Starting 2-Running 3-Off 4-Error |  | int
INPUT_REGISTER | Read | 5516 |  | DomesticHotWater Zm | Circulation Pump Running | 0 | 4 | 0-Stopping 1-Starting 2-Running 3-Off 4-Error |  | int
INPUT_REGISTER | Read | 5517 |  | DomesticHotWater Zm | Hydraulic State | 0 | 7 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Cold_load 6-Post_purge 7-Condense_protection |  | int
INPUT_REGISTER | Read | 5518 |  | DomesticHotWater Zm/Ems | Thermal Disinfection Status | 0 | 3 | 0-Off 1-On 2-Success 3-Error |  | int
INPUT_REGISTER | Read | 5519 |  | DomesticHotWater Zm/Ems | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 5520 |  | DomesticHotWater Zm/Ems | Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5521 |  | DomesticHotWater Zm/Ems | Current Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5531 |  | DomesticHotWater Fm | Charge Pump Running | 0 | 4 | 0-Stopping 1-Starting 2-Running 3-Off 4-Error |  | int
INPUT_REGISTER | Read | 5532 |  | DomesticHotWater Fm | Circulation Pump Running | 0 | 4 | 0-Stopping 1-Starting 2-Running 3-Off 4-Error |  | int
INPUT_REGISTER | Read | 5533 |  | DomesticHotWater Fm | Hydraulic State | 0 | 7 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Cold_load 6-Post_purge 7-Condense_protection |  | int
INPUT_REGISTER | Read | 5534 |  | DomesticHotWater Fm | Thermal Disinfection Status | 0 | 3 | 0-Off 1-On 2-Success 3-Error |  | int
INPUT_REGISTER | Read | 5535 |  | DomesticHotWater Fm | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 5536 |  | DomesticHotWater Fm | Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5537 |  | DomesticHotWater Fm | Current Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER |  | 5547 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 5548 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 5550 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 5552 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 5553 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 5554 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 5555 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 5556 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 5559 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 5560 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER | Read | 5563 |  | AlternativeHeatSource | Operating hours |  |  |  | h | long
INPUT_REGISTER | Read | 5565 |  | AlternativeHeatSource | Heat Source Starts |  |  |  |  | long
INPUT_REGISTER | Read | 5567 |  | AlternativeHeatSource | Heat Source Hours to Maintenance |  |  |  | h | int
INPUT_REGISTER | Read | 5569 |  | AlternativeHeatSource | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
| Read |  | 0 | AlternativeHeatSource | Is Heat Source On |  |  |  |  | bit
| Read |  | 1 | AlternativeHeatSource | Is Heat Source On Request |  |  |  |  | bit
INPUT_REGISTER | Read | 5587 |  | HydraulicCircuit Zm | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5588 |  | HydraulicCircuit Zm | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5589 |  | HydraulicCircuit Zm | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5590 |  | HydraulicCircuit Zm | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5591 |  | HydraulicCircuit Zm | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 5592 |  | HydraulicCircuit Zm | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 5593 |  | HydraulicCircuit Zm | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 5594 |  | HydraulicCircuit Zm | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 5595 |  | HydraulicCircuit Zm | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 5599 |  | HydraulicCircuit 1 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5600 |  | HydraulicCircuit 1 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5601 |  | HydraulicCircuit 1 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5602 |  | HydraulicCircuit 1 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5603 |  | HydraulicCircuit 1 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 5604 |  | HydraulicCircuit 1 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 5605 |  | HydraulicCircuit 1 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 5606 |  | HydraulicCircuit 1 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 5607 |  | HydraulicCircuit 1 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 5612 |  | HydraulicCircuit 2 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5613 |  | HydraulicCircuit 2 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5614 |  | HydraulicCircuit 2 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5615 |  | HydraulicCircuit 2 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5616 |  | HydraulicCircuit 2 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 5617 |  | HydraulicCircuit 2 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 5618 |  | HydraulicCircuit 2 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 5619 |  | HydraulicCircuit 2 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 5620 |  | HydraulicCircuit 2 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 5625 |  | HydraulicCircuit 3 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5626 |  | HydraulicCircuit 3 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5627 |  | HydraulicCircuit 3 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5628 |  | HydraulicCircuit 3 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5629 |  | HydraulicCircuit 3 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 5630 |  | HydraulicCircuit 3 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 5631 |  | HydraulicCircuit 3 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 5632 |  | HydraulicCircuit 3 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 5633 |  | HydraulicCircuit 3 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 5638 |  | HydraulicCircuit 4 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5639 |  | HydraulicCircuit 4 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5640 |  | HydraulicCircuit 4 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5641 |  | HydraulicCircuit 4 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5642 |  | HydraulicCircuit 4 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 5643 |  | HydraulicCircuit 4 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 5644 |  | HydraulicCircuit 4 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 5645 |  | HydraulicCircuit 4 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 5646 |  | HydraulicCircuit 4 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 5651 |  | HydraulicCircuit 5 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5652 |  | HydraulicCircuit 5 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5653 |  | HydraulicCircuit 5 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5654 |  | HydraulicCircuit 5 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5655 |  | HydraulicCircuit 5 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 5656 |  | HydraulicCircuit 5 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 5657 |  | HydraulicCircuit 5 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 5658 |  | HydraulicCircuit 5 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 5659 |  | HydraulicCircuit 5 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 5664 |  | HydraulicCircuit 6 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5665 |  | HydraulicCircuit 6 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5666 |  | HydraulicCircuit 6 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5667 |  | HydraulicCircuit 6 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5668 |  | HydraulicCircuit 6 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 5669 |  | HydraulicCircuit 6 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 5670 |  | HydraulicCircuit 6 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 5671 |  | HydraulicCircuit 6 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 5672 |  | HydraulicCircuit 6 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 5677 |  | HydraulicCircuit 7 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5678 |  | HydraulicCircuit 7 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5679 |  | HydraulicCircuit 7 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5680 |  | HydraulicCircuit 7 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5681 |  | HydraulicCircuit 7 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 5682 |  | HydraulicCircuit 7 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 5683 |  | HydraulicCircuit 7 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 5684 |  | HydraulicCircuit 7 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 5685 |  | HydraulicCircuit 7 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 5690 |  | HydraulicCircuit 8 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5691 |  | HydraulicCircuit 8 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5692 |  | HydraulicCircuit 8 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5693 |  | HydraulicCircuit 8 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5694 |  | HydraulicCircuit 8 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 5695 |  | HydraulicCircuit 8 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 5696 |  | HydraulicCircuit 8 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 5697 |  | HydraulicCircuit 8 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 5698 |  | HydraulicCircuit 8 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 5703 |  | i2c | Global Error State | 0 | 4 | 0-No_Error 1-i2c_driver_error 2-Wrong_Cycle_Time 3-Missing_Module_Slot 4-Module_Slot_Error |  | int
INPUT_REGISTER | Read | 5704 |  | i2c | Slot1 Module Detected |  |  | 0-Unknown 1-None 22-FM_CM 25-FM_SI 28-FM_MM 29-FM_MW 30-FM_AM 31-FM_CM2 |  | int
INPUT_REGISTER | Read | 5705 |  | i2c | Slot1 Error State |  |  | 0-No_Error 1-No_Response 2-Wrong_Module 3-Unsupported_Module 4-Internal_Sw_Error 5-Communication_Failed 6-Internal_Module_Error 7-Module_Not_Supported_Current_Variant 8-Module_Not_Suppported_In_Slot 9-Module_Count_Too_High 10-Module_Not_Supported_With_Connected_Boiler_Type |  | int
INPUT_REGISTER | Read | 5706 |  | i2c | Slot2 Module Detected |  |  | 0-Unknown 1-None 22-FM_CM 25-FM_SI 28-FM_MM 29-FM_MW 30-FM_AM 31-FM_CM2 |  | int
INPUT_REGISTER | Read | 5707 |  | i2c | Slot2 Error State |  |  | 0-No_Error 1-No_Response 2-Wrong_Module 3-Unsupported_Module 4-Internal_Sw_Error 5-Communication_Failed 6-Internal_Module_Error 7-Module_Not_Supported_Current_Variant 8-Module_Not_Suppported_In_Slot 9-Module_Count_Too_High 10-Module_Not_Supported_With_Connected_Boiler_Type |  | int
INPUT_REGISTER | Read | 5708 |  | i2c | Slot3 Module Detected |  |  | 0-Unknown 1-None 22-FM_CM 25-FM_SI 28-FM_MM 29-FM_MW 30-FM_AM 31-FM_CM2 |  | int
INPUT_REGISTER | Read | 5709 |  | i2c | Slot3 Error State |  |  | 0-No_Error 1-No_Response 2-Wrong_Module 3-Unsupported_Module 4-Internal_Sw_Error 5-Communication_Failed 6-Internal_Module_Error 7-Module_Not_Supported_Current_Variant 8-Module_Not_Suppported_In_Slot 9-Module_Count_Too_High 10-Module_Not_Supported_With_Connected_Boiler_Type |  | int
INPUT_REGISTER | Read | 5710 |  | i2c | Slot4 Module Detected |  |  | 0-Unknown 1-None 22-FM_CM 25-FM_SI 28-FM_MM 29-FM_MW 30-FM_AM 31-FM_CM2 |  | int
INPUT_REGISTER | Read | 5711 |  | i2c | Slot4 Error State |  |  | 0-No_Error 1-No_Response 2-Wrong_Module 3-Unsupported_Module 4-Internal_Sw_Error 5-Communication_Failed 6-Internal_Module_Error 7-Module_Not_Supported_Current_Variant 8-Module_Not_Suppported_In_Slot 9-Module_Count_Too_High 10-Module_Not_Supported_With_Connected_Boiler_Type |  | int
INPUT_REGISTER | Read | 5712 |  | i2c | Slot A Module Detected |  |  | 0-Unknown 1-None 26-ZM5313 27-ZM5311 |  | int
INPUT_REGISTER | Read | 5713 |  | i2c | Slot A Error State |  |  | 0-No_Error 1-No_Response 2-Wrong_Module 3-Unsupported_Module 4-Internal_Sw_Error 5-Communication_Failed 6-Internal_Module_Error 7-Module_Not_Supported_Current_Variant 8-Module_Not_Suppported_In_Slot 9-Module_Count_Too_High 10-Module_Not_Supported_With_Connected_Boiler_Type |  | int
INPUT_REGISTER | Read | 5714 |  | i2c | irBitblock |  |  |  |  | int
| Read |  | 0 | i2c | Component Error |  |  |  |  | bit
INPUT_REGISTER | Read | 5725 |  | fm-si | irBitblock |  |  |  |  | int
| Read |  | 0 | fm-si | Input 1 Error |  |  |  |  | bit
| Read |  | 1 | fm-si | Input 2 Error |  |  |  |  | bit
| Read |  | 2 | fm-si | Input 3 Error |  |  |  |  | bit
| Read |  | 3 | fm-si | Input 4 Error |  |  |  |  | bit
| Read |  | 4 | fm-si | Input 5 Error |  |  |  |  | bit
INPUT_REGISTER | Read | 5732 |  | Sdc | Demand Mode (Low Priority) | 0 | 2 | 0-Off 1-Take_Heat 2-Give_Heat |  | int
INPUT_REGISTER | Read | 5733 |  | Sdc | Demand Flow Temp (Low Priority) |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5734 |  | Sdc | Demand Mode (High Priority) | 0 | 2 | 0-Off 1-Take_Heat 2-Give_Heat |  | int
INPUT_REGISTER | Read | 5735 |  | Sdc | Demand Flow Temp (High Priority) |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5739 |  | Heat Pump | System return temperature for HP heating buffer |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5740 |  | Heat Pump | Buffer mid temperature for HP heating buffer |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5741 |  | Heat Pump | Buffer top temperature for HP heating buffer |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5742 |  | Heat Pump | Buffer bottom temperature for HP heating buffer |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5743 |  | Heat Pump | Return temperature FWR |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5744 |  | Heat Pump | Flow temperature FWV |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5745 |  | Heat Pump | Flow temperature HP |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5746 |  | Heat Pump | Return temperature HP |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5747 |  | Heat Pump | HMI State of HP Component | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 5748 |  | Heat Pump | HP current heat output |  |  |  | kW | signed int | x10
INPUT_REGISTER | Read | 5749 |  | Heat Pump | HP current electrical power consumption | 0 | 10000 |  | kW | int | x10
INPUT_REGISTER | Read | 5750 |  | Heat Pump | HP Smart grid mode | 0 | 3 | 0-normal_charging_grid 1-low_charging_grid 2-high_charging_grid 3-free_charging_grid |  | int
INPUT_REGISTER | Read | 5751 |  | Heat Pump | Heat demand temperature set point |  |  |  | °C | int
INPUT_REGISTER | Read | 5752 |  | Heat Pump | heatPumpStatusIrBitblock | 0 |  |  |  | int
INPUT_REGISTER | Read | 5753 |  | Heat Pump | Ambient Temperature HP |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5754 |  | Heat Pump | HP silent mode | 0 | 3 | 0-standard_mode 1-silent_mode 2-super_silent_mode 3-night_mode |  | int
INPUT_REGISTER | Read | 5755 |  | Heat Pump | Heat Pump Heat Request Temperature |  |  |  | °C | int
INPUT_REGISTER | Read | 5756 |  | Heat Pump | heatPumpIrBitblock |  |  |  |  | int
INPUT_REGISTER | Read | 5765 |  | System | Open Notifications Count |  |  |  |  | int
INPUT_REGISTER | Read | 5766 |  | System | Error Key 5 |  |  |  |  | long
INPUT_REGISTER | Read | 5768 |  | System | Error Key 6 |  |  |  |  | long
INPUT_REGISTER | Read | 5770 |  | System | Error Key 7 |  |  |  |  | long
INPUT_REGISTER | Read | 5772 |  | System | Error Key 8 |  |  |  |  | long
INPUT_REGISTER | Read | 5774 |  | System | Error Key 9 |  |  |  |  | long
INPUT_REGISTER | Read | 5776 |  | System | Error Key 10 |  |  |  |  | long
INPUT_REGISTER | Read | 5778 |  | Chp / EC Power | Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5779 |  | Chp / EC Power | Return Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5780 |  | Chp | Flue Gas Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5781 |  | Chp | Motor Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5782 |  | Chp / EC Power | Current Generator Power |  |  |  | kW | int
INPUT_REGISTER | Read | 5783 |  | Chp | Current Power Setpoint |  |  |  | kW | int
INPUT_REGISTER | Read | 5784 |  | Chp / EC Power | Operation Hours |  |  |  | h | long
INPUT_REGISTER | Read | 5786 |  | Chp / EC Power | Number of starts |  |  |  |  | long
INPUT_REGISTER | Read | 5788 |  | Chp / EC Power | Hours to Maintenance |  |  |  | h | int
INPUT_REGISTER | Read | 5790 |  | Chp | Output Power Setpoint |  |  |  | kW | int
INPUT_REGISTER | Read | 5791 |  | Chp | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 5796 |  | Chp | irBitblock |  |  |  |  | int
| Read |  | 0 | Chp | Warning |  |  |  |  | bit
| Read |  | 1 | Chp / EC Power | Malfunction |  |  |  |  | bit
| Read |  | 2 | Chp / EC Power | Controlled Shutdown |  |  |  |  | bit
| Read |  | 3 | Chp / EC Power | Generator On |  |  |  |  | bit
| Read |  | 4 | Chp | Automatic On |  |  |  |  | bit
| Read |  | 5 | Chp / EC Power | Automatic Ready |  |  |  |  | bit
| Read |  | 11 | Chp / EC Power | Output On Request |  |  |  |  | bit
INPUT_REGISTER | Read | 5804 |  | Water Treatment Module | Program Step |  |  | 20-140: Desalination not active 10000-10810: One time desalination 20000-20810: Automatic desalination 30000-30260: Stationary operation |  | int
INPUT_REGISTER | Read | 5805 |  | Water Treatment Module | Temperature Desalinization |  |  |  | °C | int | x10
INPUT_REGISTER | Read | 5806 |  | Water Treatment Module | Volume Flow |  |  |  | L/min | int | x10
INPUT_REGISTER | Read | 5807 |  | Water Treatment Module | Conductivity system |  |  |  | uS/cm | int | x10
INPUT_REGISTER | Read | 5808 |  | Water Treatment Module | Conductivity cartridge |  |  |  | uS/cm | int | x10
INPUT_REGISTER | Read | 5809 |  | Water Treatment Module | Cartridge Capacity |  |  |  | % | int
INPUT_REGISTER | Read | 5813 |  | Solar Data | Collector temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5814 |  | Solar Data | Temperature cylinder bottom |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5815 |  | Solar Data | Solar pump modulation setpoint |  |  |  | % | int
INPUT_REGISTER | Read | 5816 |  | Solar | Solar pump status | 0 | 19 | 1-TestMod 2-BlckProt 3-No heat 4-Ht avail 5-SolOff 6-MaxCyl 7-MaxColl 8-MinColl 9-FrostP 10-VacFct 11-SwChck 12-MixPrio 13-Switch 14-Priority 15-ThermD 16-MixCal 17-MixOpn 18-MixCl 19-MixOff |  | int
INPUT_REGISTER | Read | 5817 |  | Solar Data | Heat exchanger temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5818 |  | Solar Data | Heat exchanger pump modulation setpoint |  |  |  | % | int
INPUT_REGISTER | Read | 5819 |  | Solar | Heat exchanger pump status | 0 | 19 | 1-TestMod 2-BlckProt 3-No heat 4-Ht avail 5-SolOff 6-MaxCyl 7-MaxColl 8-MinColl 9-FrostP 10-VacFct 11-SwChck 12-MixPrio 13-Switch 14-Priority 15-ThermD 16-MixCal 17-MixOpn 18-MixCl 19-MixOff |  | int
INPUT_REGISTER | Read | 5820 |  | Solar Data | Temperature cylinder 3 top |  |  |  | °C | int | x10
INPUT_REGISTER | Read | 5821 |  | Solar Data | Reload pump modulation setpoint |  |  |  | % | int
INPUT_REGISTER | Read | 5822 |  | Solar | Reload pump status | 0 | 19 | 1-TestMod 2-BlckProt 3-No heat 4-Ht avail 5-SolOff 6-MaxCyl 7-MaxColl 8-MinColl 9-FrostP 10-VacFct 11-SwChck 12-MixPrio 13-Switch 14-Priority 15-ThermD 16-MixCal 17-MixOpn 18-MixCl 19-MixOff |  | int
INPUT_REGISTER | Read | 5823 |  | Solar | Pump therm. disinfect. status | 0 | 19 | 1-TestMod 2-BlckProt 3-No heat 4-Ht avail 5-SolOff 6-MaxCyl 7-MaxColl 8-MinColl 9-FrostP 10-VacFct 11-SwChck 12-MixPrio 13-Switch 14-Priority 15-ThermD 16-MixCal 17-MixOpn 18-MixCl 19-MixOff |  | int
INPUT_REGISTER | Read | 5824 |  | Solar Yield | Flow temperature heat meter |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5825 |  | Solar Yield | Return temperature heat meter |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5826 |  | Solar Yield | Heat count pulse counter | 0 | 15 |  |  | int
INPUT_REGISTER | Read | 5827 |  | Solar Yield | Solar yield per month |  |  |  | kWh | long | x10
INPUT_REGISTER | Read | 5829 |  | Solar Yield | Solar yield per year |  |  |  | kWh | long | x10
INPUT_REGISTER | Read | 5831 |  | Solar Yield | Last hour solar yield |  |  |  | kWh | long | x10
INPUT_REGISTER | Read | 5833 |  | Solar Yield | Solar yield per day |  |  |  | kWh | long | x10
INPUT_REGISTER | Read | 5835 |  | Solar Yield | Solar yield since installation |  |  |  | kWh | long | x10
INPUT_REGISTER | Read | 5837 |  | Solar | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 5838 |  | Solar Data | Hydraulic configuration |  |  |  |  | int
| Read |  | 0 | Solar | Option 1 active |  |  |  |  | bit
| Read |  | 1 | Solar | Option A active |  |  |  |  | bit
| Read |  | 2 | Solar | Option B active |  |  |  |  | bit
| Read |  | 3 | Solar | Option C active |  |  |  |  | bit
| Read |  | 4 | Solar | Option D active |  |  |  |  | bit
| Read |  | 5 | Solar | Option E active |  |  |  |  | bit
| Read |  | 6 | Solar | Option F active |  |  |  |  | bit
| Read |  | 7 | Solar | Option G active |  |  |  |  | bit
| Read |  | 8 | Solar | Option H active |  |  |  |  | bit
| Read |  | 9 | Solar | Option I active |  |  |  |  | bit
| Read |  | 10 | Solar | Option J active |  |  |  |  | bit
| Read |  | 11 | Solar | Option K active |  |  |  |  | bit
| Read |  | 12 | Solar | Option L active |  |  |  |  | bit
| Read |  | 13 | Solar | Option M active |  |  |  |  | bit
| Read |  | 14 | Solar | Option N active |  |  |  |  | bit
| Read |  | 15 | Solar | Option P active |  |  |  |  | bit
INPUT_REGISTER | Read | 5839 |  | Solar Data | irBitblock |  |  |  |  | int
| Read |  | 0 | Solar | Is Active |  |  |  |  | bit
INPUT_REGISTER |  | 5900 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 5901 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 5902 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 5903 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 5904 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 5905 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 5906 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 5907 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 5908 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 5909 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 5910 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 5911 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 5912 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 5913 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER | Read | 5922 |  | Energy Monitoring | Heat Output |  |  |  | kW | signed int | x10
INPUT_REGISTER | Read | 5923 |  | Energy Monitoring | Gas Consumption (LCV) |  |  |  | kW | signed int | x10
INPUT_REGISTER | Read | 5925 |  | Energy Monitoring | Electrical Power |  |  |  | W | int
INPUT_REGISTER | Read | 5930 |  | Fresh Water Characteristics 1 | DHW Out Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5931 |  | Fresh Water Characteristics 1 | DHW Volume Flow |  |  |  | L/min | signed int | x10
INPUT_REGISTER | Read | 5932 |  | Fresh Water Characteristics 1 | Prim In Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5933 |  | Fresh Water Characteristics 1 | DHW In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5934 |  | Fresh Water Characteristics 1 | Primary Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 5935 |  | Fresh Water Characteristics 1 | Request DHW Out Temperature |  |  |  | °C | int
INPUT_REGISTER | Read | 5936 |  | Fresh Water Characteristics 1 | Status Request DHW Out Temperature | 0 | 9 | 0-Off 1-DHWRed 2-DHW 3-Sol_red 4-Once_on 5-Therm_d 6-DlyHtUp 7-Preheat_start 8-Preheat_normal 9-No_eq |  | int
INPUT_REGISTER | Read | 5937 |  | Fresh Water Characteristics 2 | Circulation Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 5938 |  | Fresh Water Characteristics 2 | Status Circulation Pump | 0 | 8 | 0-Undefined 1-Test 2-BlckProt 3-No_req 4-AutoOff 5-AutoOn 6-Therm_d 7-Sys_Off 8-DlyHtUp |  | int
INPUT_REGISTER | Read | 5939 |  | Fresh Water Characteristics 2 | Return Valve Modulation Request |  |  |  | % | int
INPUT_REGISTER | Read | 5940 |  | Fresh Water Characteristics 2 | Valve State | 0 | 5 | 0-Undefined 1-TestMod 2-BlckProt 3-Mix_cl 4-Mix_opn 5-Sys_Off |  | int
INPUT_REGISTER | Read | 5941 |  | Fresh Water Characteristics 2 | Return Valve Buffer Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5942 |  | Fresh Water Characteristics 2 | Disinfection Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 5943 |  | Fresh Water Characteristics 2 | Pump State | 0 | 5 | 0-Undefined 1-TestMod 2-BlckPro 3-No_eq 4-Ht_req 5-Sys_Off |  | int
INPUT_REGISTER | Read | 5944 |  | Fresh Water Characteristics 1 | DHW Valve Power |  |  |  | % | int
INPUT_REGISTER | Read | 5945 |  | Fresh Water Characteristics 2 | Total Flow |  |  |  | L/min | int | x10
INPUT_REGISTER | Read | 5946 |  | Fresh Water 2 | Module 2 DHW Out Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5947 |  | Fresh Water 2 | Module 2 DHW Volume Flow |  |  |  | L/min | signed int | x10
INPUT_REGISTER | Read | 5948 |  | Fresh Water 2 | Module 2 Prim In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5949 |  | Fresh Water 2 | Module 2 DHW In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5950 |  | Fresh Water 2 | Module 2 DHW Valve Power |  |  |  | % | int
INPUT_REGISTER | Read | 5951 |  | Fresh Water 2 | Module 2 Prim Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 5952 |  | Fresh Water 2 | Module 2 Status Prim Pump |  |  |  |  | int
INPUT_REGISTER | Read | 5953 |  | Fresh Water 3 | Module 3 DHW Out Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5954 |  | Fresh Water 3 | Module 3 DHW Volume Flow |  |  |  | L/min | signed int | x10
INPUT_REGISTER | Read | 5955 |  | Fresh Water 3 | Module 3 Prim In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5956 |  | Fresh Water 3 | Module 3 DHW In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5957 |  | Fresh Water 3 | Module 3 DHW Valve Power |  |  |  | % | int
INPUT_REGISTER | Read | 5958 |  | Fresh Water 3 | Module 3 Prim Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 5959 |  | Fresh Water 3 | Module 3 Status Prim Pump |  |  |  |  | int
INPUT_REGISTER | Read | 5960 |  | Fresh Water 4 | Module 4 DHW Out Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5961 |  | Fresh Water 4 | Module 4 DHW Volume Flow |  |  |  | L/min | signed int | x10
INPUT_REGISTER | Read | 5962 |  | Fresh Water 4 | Module 4 Prim In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5963 |  | Fresh Water 4 | Module 4 DHW In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 5964 |  | Fresh Water 4 | Module 4 DHW ValvePower |  |  |  | % | int
INPUT_REGISTER | Read | 5965 |  | Fresh Water 4 | Module 4 Prim Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 5966 |  | Fresh Water 4 | Module 4 Status Primary Pump |  |  |  |  | int
INPUT_REGISTER | Read | 5967 |  | Fresh Water | Fresh Water Hmi State |  |  |  |  | int
INPUT_REGISTER | Read | 5968 |  | Fresh Water Characteristics 3 | Fresh Water Configurations |  |  |  |  | int
| Read |  | 0 | Fresh Water | Option 2 active |  |  |  |  | bit
| Read |  | 1 | Fresh Water | Option A active |  |  |  |  | bit
| Read |  | 2 | Fresh Water | Option B active |  |  |  |  | bit
| Read |  | 3 | Fresh Water | Option C active |  |  |  |  | bit
| Read |  | 4 | Fresh Water | Option D active |  |  |  |  | bit
| Read |  | 5 | Fresh Water | Option E active |  |  |  |  | bit
| Read |  | 6 | Fresh Water | Option E active cascade module 2 active |  |  |  |  | bit
| Read |  | 7 | Fresh Water | Option E active cascade module 3 active |  |  |  |  | bit
| Read |  | 8 | Fresh Water | Option E active cascade module 4 active |  |  |  |  | bit
| Read |  | 9 | Fresh Water | Is Active |  |  |  |  | bit
INPUT_REGISTER | Read | 5976 |  | System | Error Key 1 |  |  |  |  | long
INPUT_REGISTER | Read | 5978 |  | System | Error Key 2 |  |  |  |  | long
INPUT_REGISTER | Read | 5980 |  | System | Error Key 3 |  |  |  |  | long
INPUT_REGISTER | Read | 5982 |  | System | Error Key 4 |  |  |  |  | long
INPUT_REGISTER | Read | 5984 |  | System | Error 1 Extra Info (MSB) |  |  |  |  | long
INPUT_REGISTER | Read | 5986 |  | System | Error 1 Extra Info (LSB) |  |  |  |  | long
INPUT_REGISTER | Read | 5988 |  | System | Error 2 Extra Info (MSB) |  |  |  |  | long
INPUT_REGISTER | Read | 5990 |  | System | Error 2 Extra Info (LSB) |  |  |  |  | long
INPUT_REGISTER | Read | 5992 |  | System | Error 3 Extra Info (MSB) |  |  |  |  | long
INPUT_REGISTER | Read | 5994 |  | System | Error 3 Extra Info (LSB) |  |  |  |  | long
INPUT_REGISTER | Read | 5996 |  | System | Error 4 Extra Info (MSB) |  |  |  |  | long
INPUT_REGISTER | Read | 5998 |  | System | Error 4 Extra Info (LSB) |  |  |  |  | long

## Slave12
Register Type | Permissions | Address | Bitblock Bit | Component | Name | Min | Max | Range | Unit | DataType | Float to Int Factor
HOLDING_REGISTER | Write | 6007 |  | DomesticHotWater Zm/Ems | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 6008 |  | DomesticHotWater Zm/Ems | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 6009 |  | DomesticHotWater Zm/Ems | Thermal Disinfection Setpoint | 65 | 75 |  | °C | int | x10
HOLDING_REGISTER | Write | 6010 |  | DomesticHotWater Zm | Setpoint Auto Day | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 6011 |  | DomesticHotWater Zm | Setpoint Auto Night | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 6012 |  | DomesticHotWater Zm | Setpoint Manual Day | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 6013 |  | DomesticHotWater Zm | Setpoint Manual Night | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 6014 |  | DomesticHotWater Zm | Setpoint Holiday | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 6015 |  | DomesticHotWater Zm/Ems | Circulation Pump Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 6016 |  | DomesticHotWater Zm/Ems | Circulation Pump Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 6017 |  | DomesticHotWater Zm/Ems | Disinfection Frequency | 0 | 7 | 0-Daily 1-Monday 2-Tuesday 3-Wednesday 4-Thursday 5-Friday 6-Saturday 7-Sunday |  | int
HOLDING_REGISTER | Write | 6018 |  | DomesticHotWater Zm/Ems | Disinfection Start Hour | 0 | 23 |  | h | int
HOLDING_REGISTER | Write | 6021 |  | DomesticHotWater Fm | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 6022 |  | DomesticHotWater Fm | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 6023 |  | DomesticHotWater Fm | Thermal Disinfection Setpoint | 65 | 75 |  | °C | int | x10
HOLDING_REGISTER | Write | 6024 |  | DomesticHotWater Fm | Setpoint Auto Day | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 6025 |  | DomesticHotWater Fm | Setpoint Auto Night | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 6026 |  | DomesticHotWater Fm | Setpoint Manual Day | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 6027 |  | DomesticHotWater Fm | Setpoint Manual Night | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 6028 |  | DomesticHotWater Fm | Setpoint Holiday | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 6029 |  | DomesticHotWater Fm | Circulation Pump Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 6030 |  | DomesticHotWater Fm | Circulation Pump Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 6031 |  | DomesticHotWater Fm | Disinfection Frequency | 0 | 7 | 0-Daily 1-Monday 2-Tuesday 3-Wednesday 4-Thursday 5-Friday 6-Saturday 7-Sunday |  | int
HOLDING_REGISTER | Write | 6032 |  | DomesticHotWater Fm | Disinfection Start Hour | 0 | 23 |  | h | int
HOLDING_REGISTER | Read | 6039 |  | Boiler | Control Type | 0 | 4 | 0-None 1-Safe 2-Ems 3-7Pole 4-Substation |  | int
HOLDING_REGISTER | Write | 6043 |  | AlternativeHeatSource | Operation Mode Request Auto Day | 20 | 99 |  | °C | int
HOLDING_REGISTER | Write | 6044 |  | AlternativeHeatSource | Operation Mode Request Auto Night | 20 | 99 |  | °C | int
HOLDING_REGISTER | Write | 6045 |  | AlternativeHeatSource | Operation Mode Request Manual Day | 20 | 99 |  | °C | int
HOLDING_REGISTER | Write | 6046 |  | AlternativeHeatSource | Operation Mode Request Manual Night | 20 | 99 |  | °C | int
HOLDING_REGISTER | Write | 6047 |  | AlternativeHeatSource | Operation Mode Request Holiday | 20 | 99 |  | °C | int
HOLDING_REGISTER | Write | 6048 |  | AlternativeHeatSource | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 6049 |  | AlternativeHeatSource | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 6050 |  | AlternativeHeatSource | Return Control Setpoint User | 10 | 70 |  | °C | int
HOLDING_REGISTER | Write | 6057 |  | HydraulicCircuit Zm | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 6058 |  | HydraulicCircuit Zm | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 6059 |  | HydraulicCircuit Zm | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6060 |  | HydraulicCircuit Zm | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6061 |  | HydraulicCircuit Zm | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6062 |  | HydraulicCircuit Zm | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6063 |  | HydraulicCircuit Zm | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6064 |  | HydraulicCircuit Zm | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 6070 |  | HydraulicCircuit 1 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 6071 |  | HydraulicCircuit 1 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 6072 |  | HydraulicCircuit 1 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6073 |  | HydraulicCircuit 1 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6074 |  | HydraulicCircuit 1 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6075 |  | HydraulicCircuit 1 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6076 |  | HydraulicCircuit 1 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6077 |  | HydraulicCircuit 1 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 6083 |  | HydraulicCircuit 2 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 6084 |  | HydraulicCircuit 2 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 6085 |  | HydraulicCircuit 2 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6086 |  | HydraulicCircuit 2 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6087 |  | HydraulicCircuit 2 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6088 |  | HydraulicCircuit 2 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6089 |  | HydraulicCircuit 2 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6090 |  | HydraulicCircuit 2 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 6096 |  | HydraulicCircuit 3 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 6097 |  | HydraulicCircuit 3 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 6098 |  | HydraulicCircuit 3 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6099 |  | HydraulicCircuit 3 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6100 |  | HydraulicCircuit 3 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6101 |  | HydraulicCircuit 3 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6102 |  | HydraulicCircuit 3 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6103 |  | HydraulicCircuit 3 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 6109 |  | HydraulicCircuit 4 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 6110 |  | HydraulicCircuit 4 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 6111 |  | HydraulicCircuit 4 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6112 |  | HydraulicCircuit 4 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6113 |  | HydraulicCircuit 4 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6114 |  | HydraulicCircuit 4 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6115 |  | HydraulicCircuit 4 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6116 |  | HydraulicCircuit 4 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 6122 |  | HydraulicCircuit 5 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 6123 |  | HydraulicCircuit 5 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 6124 |  | HydraulicCircuit 5 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6125 |  | HydraulicCircuit 5 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6126 |  | HydraulicCircuit 5 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6127 |  | HydraulicCircuit 5 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6128 |  | HydraulicCircuit 5 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6129 |  | HydraulicCircuit 5 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 6135 |  | HydraulicCircuit 6 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 6136 |  | HydraulicCircuit 6 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 6137 |  | HydraulicCircuit 6 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6138 |  | HydraulicCircuit 6 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6139 |  | HydraulicCircuit 6 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6140 |  | HydraulicCircuit 6 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6141 |  | HydraulicCircuit 6 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6142 |  | HydraulicCircuit 6 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 6148 |  | HydraulicCircuit 7 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 6149 |  | HydraulicCircuit 7 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 6150 |  | HydraulicCircuit 7 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6151 |  | HydraulicCircuit 7 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6152 |  | HydraulicCircuit 7 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6153 |  | HydraulicCircuit 7 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6154 |  | HydraulicCircuit 7 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6155 |  | HydraulicCircuit 7 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 6161 |  | HydraulicCircuit 8 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 6162 |  | HydraulicCircuit 8 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 6163 |  | HydraulicCircuit 8 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6164 |  | HydraulicCircuit 8 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6165 |  | HydraulicCircuit 8 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6166 |  | HydraulicCircuit 8 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6167 |  | HydraulicCircuit 8 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6168 |  | HydraulicCircuit 8 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 6201 |  | Heat Pump | Heat demand source | 0 | 2 | 0-Scheduler 1-System 2-Max_system_scheduler |  | int
HOLDING_REGISTER | Read | 6421 |  | Fresh Water Characteristics 3 | DHU Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 6422 |  | Fresh Water Characteristics 3 | Extra Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 6423 |  | Fresh Water Characteristics 3 | Maximum DHW Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 6424 |  | Fresh Water Characteristics 3 | On High Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 6425 |  | Fresh Water Characteristics 3 | On Low Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 6426 |  | Fresh Water Characteristics 3 | Fresh Water Type | 0 | 3 | 0-15/20l/min 1-27l/min 2-40l/min 3-60l/min |  | int
HOLDING_REGISTER | Read | 6427 |  | Fresh Water Characteristics 3 | Enable Alarm Output | 0 | 2 | 0-No 1-Yes 2-Inverted |  | int
HOLDING_REGISTER | Read | 6428 |  | Fresh Water Characteristics 3 | Buffer Cylinder Temperature Offset |  |  |  | K | int
HOLDING_REGISTER | Read | 6429 |  | Fresh Water Characteristics 3 | hrBitblock |  |  |  |  | int
| Read |  | 0 | Fresh Water | Buffer Cylinder Temperature Optimization Enabled |  |  |  |  | bit
| Read |  | 1 | Fresh Water | Impulse Enabled |  |  |  |  | bit
| Read |  | 2 | Fresh Water | Time Program Enabled |  |  |  |  | bit
HOLDING_REGISTER | Read | 6430 |  | Fresh Water Characteristics 3 | Minimum Buffer Cylinder Temperature Offset |  |  |  | K | int
HOLDING_REGISTER | Read | 6431 |  | Fresh Water Characteristics 2 | Circulation Pump Runs per Hour | 0 | 7 | 0-Undefined 1-1x3_minutes/h 2-2x3_minutes/h 3-3x3_minutes/h 4-4x3_minutes/h 5-5x3_minutes/h 6-6x3_minutes/h 7-Permanent |  | int
HOLDING_REGISTER | Read | 6432 |  | Fresh Water Characteristics 2 | Swich Hysteresis |  |  |  | K | int
HOLDING_REGISTER | Read | 6433 |  | Fresh Water Characteristics 2 | Thermal Disinfection Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 6434 |  | Fresh Water Characteristics 2 | Pre Heat Maximum Temperature |  |  |  | °C | int
INPUT_REGISTER | Read | 6000 |  | System | Own Outdoor temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6001 |  | System | Damped Own outdoor temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6004 |  | System | Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6008 |  | System | Active Functions 1 |  |  |  |  | int
INPUT_REGISTER | Read | 6009 |  | System | Active Functions 2 |  |  |  |  | int
INPUT_REGISTER | Read | 6015 |  | DomesticHotWater Zm | Charge Pump Running | 0 | 4 | 0-Stopping 1-Starting 2-Running 3-Off 4-Error |  | int
INPUT_REGISTER | Read | 6016 |  | DomesticHotWater Zm | Circulation Pump Running | 0 | 4 | 0-Stopping 1-Starting 2-Running 3-Off 4-Error |  | int
INPUT_REGISTER | Read | 6017 |  | DomesticHotWater Zm | Hydraulic State | 0 | 7 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Cold_load 6-Post_purge 7-Condense_protection |  | int
INPUT_REGISTER | Read | 6018 |  | DomesticHotWater Zm/Ems | Thermal Disinfection Status | 0 | 3 | 0-Off 1-On 2-Success 3-Error |  | int
INPUT_REGISTER | Read | 6019 |  | DomesticHotWater Zm/Ems | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 6020 |  | DomesticHotWater Zm/Ems | Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6021 |  | DomesticHotWater Zm/Ems | Current Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6031 |  | DomesticHotWater Fm | Charge Pump Running | 0 | 4 | 0-Stopping 1-Starting 2-Running 3-Off 4-Error |  | int
INPUT_REGISTER | Read | 6032 |  | DomesticHotWater Fm | Circulation Pump Running | 0 | 4 | 0-Stopping 1-Starting 2-Running 3-Off 4-Error |  | int
INPUT_REGISTER | Read | 6033 |  | DomesticHotWater Fm | Hydraulic State | 0 | 7 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Cold_load 6-Post_purge 7-Condense_protection |  | int
INPUT_REGISTER | Read | 6034 |  | DomesticHotWater Fm | Thermal Disinfection Status | 0 | 3 | 0-Off 1-On 2-Success 3-Error |  | int
INPUT_REGISTER | Read | 6035 |  | DomesticHotWater Fm | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 6036 |  | DomesticHotWater Fm | Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6037 |  | DomesticHotWater Fm | Current Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER |  | 6047 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 6048 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 6050 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 6052 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 6053 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 6054 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 6055 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 6056 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 6059 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 6060 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER | Read | 6063 |  | AlternativeHeatSource | Operating hours |  |  |  | h | long
INPUT_REGISTER | Read | 6065 |  | AlternativeHeatSource | Heat Source Starts |  |  |  |  | long
INPUT_REGISTER | Read | 6067 |  | AlternativeHeatSource | Heat Source Hours to Maintenance |  |  |  | h | int
INPUT_REGISTER | Read | 6069 |  | AlternativeHeatSource | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
| Read |  | 0 | AlternativeHeatSource | Is Heat Source On |  |  |  |  | bit
| Read |  | 1 | AlternativeHeatSource | Is Heat Source On Request |  |  |  |  | bit
INPUT_REGISTER | Read | 6087 |  | HydraulicCircuit Zm | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6088 |  | HydraulicCircuit Zm | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6089 |  | HydraulicCircuit Zm | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6090 |  | HydraulicCircuit Zm | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6091 |  | HydraulicCircuit Zm | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 6092 |  | HydraulicCircuit Zm | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 6093 |  | HydraulicCircuit Zm | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 6094 |  | HydraulicCircuit Zm | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 6095 |  | HydraulicCircuit Zm | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 6099 |  | HydraulicCircuit 1 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6100 |  | HydraulicCircuit 1 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6101 |  | HydraulicCircuit 1 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6102 |  | HydraulicCircuit 1 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6103 |  | HydraulicCircuit 1 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 6104 |  | HydraulicCircuit 1 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 6105 |  | HydraulicCircuit 1 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 6106 |  | HydraulicCircuit 1 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 6107 |  | HydraulicCircuit 1 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 6112 |  | HydraulicCircuit 2 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6113 |  | HydraulicCircuit 2 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6114 |  | HydraulicCircuit 2 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6115 |  | HydraulicCircuit 2 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6116 |  | HydraulicCircuit 2 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 6117 |  | HydraulicCircuit 2 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 6118 |  | HydraulicCircuit 2 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 6119 |  | HydraulicCircuit 2 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 6120 |  | HydraulicCircuit 2 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 6125 |  | HydraulicCircuit 3 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6126 |  | HydraulicCircuit 3 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6127 |  | HydraulicCircuit 3 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6128 |  | HydraulicCircuit 3 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6129 |  | HydraulicCircuit 3 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 6130 |  | HydraulicCircuit 3 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 6131 |  | HydraulicCircuit 3 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 6132 |  | HydraulicCircuit 3 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 6133 |  | HydraulicCircuit 3 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 6138 |  | HydraulicCircuit 4 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6139 |  | HydraulicCircuit 4 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6140 |  | HydraulicCircuit 4 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6141 |  | HydraulicCircuit 4 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6142 |  | HydraulicCircuit 4 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 6143 |  | HydraulicCircuit 4 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 6144 |  | HydraulicCircuit 4 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 6145 |  | HydraulicCircuit 4 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 6146 |  | HydraulicCircuit 4 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 6151 |  | HydraulicCircuit 5 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6152 |  | HydraulicCircuit 5 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6153 |  | HydraulicCircuit 5 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6154 |  | HydraulicCircuit 5 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6155 |  | HydraulicCircuit 5 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 6156 |  | HydraulicCircuit 5 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 6157 |  | HydraulicCircuit 5 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 6158 |  | HydraulicCircuit 5 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 6159 |  | HydraulicCircuit 5 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 6164 |  | HydraulicCircuit 6 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6165 |  | HydraulicCircuit 6 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6166 |  | HydraulicCircuit 6 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6167 |  | HydraulicCircuit 6 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6168 |  | HydraulicCircuit 6 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 6169 |  | HydraulicCircuit 6 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 6170 |  | HydraulicCircuit 6 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 6171 |  | HydraulicCircuit 6 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 6172 |  | HydraulicCircuit 6 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 6177 |  | HydraulicCircuit 7 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6178 |  | HydraulicCircuit 7 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6179 |  | HydraulicCircuit 7 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6180 |  | HydraulicCircuit 7 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6181 |  | HydraulicCircuit 7 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 6182 |  | HydraulicCircuit 7 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 6183 |  | HydraulicCircuit 7 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 6184 |  | HydraulicCircuit 7 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 6185 |  | HydraulicCircuit 7 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 6190 |  | HydraulicCircuit 8 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6191 |  | HydraulicCircuit 8 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6192 |  | HydraulicCircuit 8 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6193 |  | HydraulicCircuit 8 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6194 |  | HydraulicCircuit 8 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 6195 |  | HydraulicCircuit 8 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 6196 |  | HydraulicCircuit 8 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 6197 |  | HydraulicCircuit 8 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 6198 |  | HydraulicCircuit 8 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 6203 |  | i2c | Global Error State | 0 | 4 | 0-No_Error 1-i2c_driver_error 2-Wrong_Cycle_Time 3-Missing_Module_Slot 4-Module_Slot_Error |  | int
INPUT_REGISTER | Read | 6204 |  | i2c | Slot1 Module Detected |  |  | 0-Unknown 1-None 22-FM_CM 25-FM_SI 28-FM_MM 29-FM_MW 30-FM_AM 31-FM_CM2 |  | int
INPUT_REGISTER | Read | 6205 |  | i2c | Slot1 Error State |  |  | 0-No_Error 1-No_Response 2-Wrong_Module 3-Unsupported_Module 4-Internal_Sw_Error 5-Communication_Failed 6-Internal_Module_Error 7-Module_Not_Supported_Current_Variant 8-Module_Not_Suppported_In_Slot 9-Module_Count_Too_High 10-Module_Not_Supported_With_Connected_Boiler_Type |  | int
INPUT_REGISTER | Read | 6206 |  | i2c | Slot2 Module Detected |  |  | 0-Unknown 1-None 22-FM_CM 25-FM_SI 28-FM_MM 29-FM_MW 30-FM_AM 31-FM_CM2 |  | int
INPUT_REGISTER | Read | 6207 |  | i2c | Slot2 Error State |  |  | 0-No_Error 1-No_Response 2-Wrong_Module 3-Unsupported_Module 4-Internal_Sw_Error 5-Communication_Failed 6-Internal_Module_Error 7-Module_Not_Supported_Current_Variant 8-Module_Not_Suppported_In_Slot 9-Module_Count_Too_High 10-Module_Not_Supported_With_Connected_Boiler_Type |  | int
INPUT_REGISTER | Read | 6208 |  | i2c | Slot3 Module Detected |  |  | 0-Unknown 1-None 22-FM_CM 25-FM_SI 28-FM_MM 29-FM_MW 30-FM_AM 31-FM_CM2 |  | int
INPUT_REGISTER | Read | 6209 |  | i2c | Slot3 Error State |  |  | 0-No_Error 1-No_Response 2-Wrong_Module 3-Unsupported_Module 4-Internal_Sw_Error 5-Communication_Failed 6-Internal_Module_Error 7-Module_Not_Supported_Current_Variant 8-Module_Not_Suppported_In_Slot 9-Module_Count_Too_High 10-Module_Not_Supported_With_Connected_Boiler_Type |  | int
INPUT_REGISTER | Read | 6210 |  | i2c | Slot4 Module Detected |  |  | 0-Unknown 1-None 22-FM_CM 25-FM_SI 28-FM_MM 29-FM_MW 30-FM_AM 31-FM_CM2 |  | int
INPUT_REGISTER | Read | 6211 |  | i2c | Slot4 Error State |  |  | 0-No_Error 1-No_Response 2-Wrong_Module 3-Unsupported_Module 4-Internal_Sw_Error 5-Communication_Failed 6-Internal_Module_Error 7-Module_Not_Supported_Current_Variant 8-Module_Not_Suppported_In_Slot 9-Module_Count_Too_High 10-Module_Not_Supported_With_Connected_Boiler_Type |  | int
INPUT_REGISTER | Read | 6212 |  | i2c | Slot A Module Detected |  |  | 0-Unknown 1-None 26-ZM5313 27-ZM5311 |  | int
INPUT_REGISTER | Read | 6213 |  | i2c | Slot A Error State |  |  | 0-No_Error 1-No_Response 2-Wrong_Module 3-Unsupported_Module 4-Internal_Sw_Error 5-Communication_Failed 6-Internal_Module_Error 7-Module_Not_Supported_Current_Variant 8-Module_Not_Suppported_In_Slot 9-Module_Count_Too_High 10-Module_Not_Supported_With_Connected_Boiler_Type |  | int
INPUT_REGISTER | Read | 6214 |  | i2c | irBitblock |  |  |  |  | int
| Read |  | 0 | i2c | Component Error |  |  |  |  | bit
INPUT_REGISTER | Read | 6225 |  | fm-si | irBitblock |  |  |  |  | int
| Read |  | 0 | fm-si | Input 1 Error |  |  |  |  | bit
| Read |  | 1 | fm-si | Input 2 Error |  |  |  |  | bit
| Read |  | 2 | fm-si | Input 3 Error |  |  |  |  | bit
| Read |  | 3 | fm-si | Input 4 Error |  |  |  |  | bit
| Read |  | 4 | fm-si | Input 5 Error |  |  |  |  | bit
INPUT_REGISTER | Read | 6232 |  | Sdc | Demand Mode (Low Priority) | 0 | 2 | 0-Off 1-Take_Heat 2-Give_Heat |  | int
INPUT_REGISTER | Read | 6233 |  | Sdc | Demand Flow Temp (Low Priority) |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6234 |  | Sdc | Demand Mode (High Priority) | 0 | 2 | 0-Off 1-Take_Heat 2-Give_Heat |  | int
INPUT_REGISTER | Read | 6235 |  | Sdc | Demand Flow Temp (High Priority) |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6239 |  | Heat Pump | System return temperature for HP heating buffer |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6240 |  | Heat Pump | Buffer mid temperature for HP heating buffer |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6241 |  | Heat Pump | Buffer top temperature for HP heating buffer |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6242 |  | Heat Pump | Buffer bottom temperature for HP heating buffer |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6243 |  | Heat Pump | Return temperature FWR |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6244 |  | Heat Pump | Flow temperature FWV |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6245 |  | Heat Pump | Flow temperature HP |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6246 |  | Heat Pump | Return temperature HP |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6247 |  | Heat Pump | HMI State of HP Component | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 6248 |  | Heat Pump | HP current heat output |  |  |  | kW | signed int | x10
INPUT_REGISTER | Read | 6249 |  | Heat Pump | HP current electrical power consumption | 0 | 10000 |  | kW | int | x10
INPUT_REGISTER | Read | 6250 |  | Heat Pump | HP Smart grid mode | 0 | 3 | 0-normal_charging_grid 1-low_charging_grid 2-high_charging_grid 3-free_charging_grid |  | int
INPUT_REGISTER | Read | 6251 |  | Heat Pump | Heat demand temperature set point |  |  |  | °C | int
INPUT_REGISTER | Read | 6252 |  | Heat Pump | heatPumpStatusIrBitblock | 0 |  |  |  | int
INPUT_REGISTER | Read | 6253 |  | Heat Pump | Ambient Temperature HP |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6254 |  | Heat Pump | HP silent mode | 0 | 3 | 0-standard_mode 1-silent_mode 2-super_silent_mode 3-night_mode |  | int
INPUT_REGISTER | Read | 6255 |  | Heat Pump | Heat Pump Heat Request Temperature |  |  |  | °C | int
INPUT_REGISTER | Read | 6256 |  | Heat Pump | heatPumpIrBitblock |  |  |  |  | int
INPUT_REGISTER | Read | 6265 |  | System | Open Notifications Count |  |  |  |  | int
INPUT_REGISTER | Read | 6266 |  | System | Error Key 5 |  |  |  |  | long
INPUT_REGISTER | Read | 6268 |  | System | Error Key 6 |  |  |  |  | long
INPUT_REGISTER | Read | 6270 |  | System | Error Key 7 |  |  |  |  | long
INPUT_REGISTER | Read | 6272 |  | System | Error Key 8 |  |  |  |  | long
INPUT_REGISTER | Read | 6274 |  | System | Error Key 9 |  |  |  |  | long
INPUT_REGISTER | Read | 6276 |  | System | Error Key 10 |  |  |  |  | long
INPUT_REGISTER | Read | 6278 |  | Chp / EC Power | Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6279 |  | Chp / EC Power | Return Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6280 |  | Chp | Flue Gas Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6281 |  | Chp | Motor Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6282 |  | Chp / EC Power | Current Generator Power |  |  |  | kW | int
INPUT_REGISTER | Read | 6283 |  | Chp | Current Power Setpoint |  |  |  | kW | int
INPUT_REGISTER | Read | 6284 |  | Chp / EC Power | Operation Hours |  |  |  | h | long
INPUT_REGISTER | Read | 6286 |  | Chp / EC Power | Number of starts |  |  |  |  | long
INPUT_REGISTER | Read | 6288 |  | Chp / EC Power | Hours to Maintenance |  |  |  | h | int
INPUT_REGISTER | Read | 6290 |  | Chp | Output Power Setpoint |  |  |  | kW | int
INPUT_REGISTER | Read | 6291 |  | Chp | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 6296 |  | Chp | irBitblock |  |  |  |  | int
| Read |  | 0 | Chp | Warning |  |  |  |  | bit
| Read |  | 1 | Chp / EC Power | Malfunction |  |  |  |  | bit
| Read |  | 2 | Chp / EC Power | Controlled Shutdown |  |  |  |  | bit
| Read |  | 3 | Chp / EC Power | Generator On |  |  |  |  | bit
| Read |  | 4 | Chp | Automatic On |  |  |  |  | bit
| Read |  | 5 | Chp / EC Power | Automatic Ready |  |  |  |  | bit
| Read |  | 11 | Chp / EC Power | Output On Request |  |  |  |  | bit
INPUT_REGISTER | Read | 6304 |  | Water Treatment Module | Program Step |  |  | 20-140: Desalination not active 10000-10810: One time desalination 20000-20810: Automatic desalination 30000-30260: Stationary operation |  | int
INPUT_REGISTER | Read | 6305 |  | Water Treatment Module | Temperature Desalinization |  |  |  | °C | int | x10
INPUT_REGISTER | Read | 6306 |  | Water Treatment Module | Volume Flow |  |  |  | L/min | int | x10
INPUT_REGISTER | Read | 6307 |  | Water Treatment Module | Conductivity system |  |  |  | uS/cm | int | x10
INPUT_REGISTER | Read | 6308 |  | Water Treatment Module | Conductivity cartridge |  |  |  | uS/cm | int | x10
INPUT_REGISTER | Read | 6309 |  | Water Treatment Module | Cartridge Capacity |  |  |  | % | int
INPUT_REGISTER | Read | 6313 |  | Solar Data | Collector temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6314 |  | Solar Data | Temperature cylinder bottom |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6315 |  | Solar Data | Solar pump modulation setpoint |  |  |  | % | int
INPUT_REGISTER | Read | 6316 |  | Solar | Solar pump status | 0 | 19 | 1-TestMod 2-BlckProt 3-No heat 4-Ht avail 5-SolOff 6-MaxCyl 7-MaxColl 8-MinColl 9-FrostP 10-VacFct 11-SwChck 12-MixPrio 13-Switch 14-Priority 15-ThermD 16-MixCal 17-MixOpn 18-MixCl 19-MixOff |  | int
INPUT_REGISTER | Read | 6317 |  | Solar Data | Heat exchanger temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6318 |  | Solar Data | Heat exchanger pump modulation setpoint |  |  |  | % | int
INPUT_REGISTER | Read | 6319 |  | Solar | Heat exchanger pump status | 0 | 19 | 1-TestMod 2-BlckProt 3-No heat 4-Ht avail 5-SolOff 6-MaxCyl 7-MaxColl 8-MinColl 9-FrostP 10-VacFct 11-SwChck 12-MixPrio 13-Switch 14-Priority 15-ThermD 16-MixCal 17-MixOpn 18-MixCl 19-MixOff |  | int
INPUT_REGISTER | Read | 6320 |  | Solar Data | Temperature cylinder 3 top |  |  |  | °C | int | x10
INPUT_REGISTER | Read | 6321 |  | Solar Data | Reload pump modulation setpoint |  |  |  | % | int
INPUT_REGISTER | Read | 6322 |  | Solar | Reload pump status | 0 | 19 | 1-TestMod 2-BlckProt 3-No heat 4-Ht avail 5-SolOff 6-MaxCyl 7-MaxColl 8-MinColl 9-FrostP 10-VacFct 11-SwChck 12-MixPrio 13-Switch 14-Priority 15-ThermD 16-MixCal 17-MixOpn 18-MixCl 19-MixOff |  | int
INPUT_REGISTER | Read | 6323 |  | Solar | Pump therm. disinfect. status | 0 | 19 | 1-TestMod 2-BlckProt 3-No heat 4-Ht avail 5-SolOff 6-MaxCyl 7-MaxColl 8-MinColl 9-FrostP 10-VacFct 11-SwChck 12-MixPrio 13-Switch 14-Priority 15-ThermD 16-MixCal 17-MixOpn 18-MixCl 19-MixOff |  | int
INPUT_REGISTER | Read | 6324 |  | Solar Yield | Flow temperature heat meter |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6325 |  | Solar Yield | Return temperature heat meter |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6326 |  | Solar Yield | Heat count pulse counter | 0 | 15 |  |  | int
INPUT_REGISTER | Read | 6327 |  | Solar Yield | Solar yield per month |  |  |  | kWh | long | x10
INPUT_REGISTER | Read | 6329 |  | Solar Yield | Solar yield per year |  |  |  | kWh | long | x10
INPUT_REGISTER | Read | 6331 |  | Solar Yield | Last hour solar yield |  |  |  | kWh | long | x10
INPUT_REGISTER | Read | 6333 |  | Solar Yield | Solar yield per day |  |  |  | kWh | long | x10
INPUT_REGISTER | Read | 6335 |  | Solar Yield | Solar yield since installation |  |  |  | kWh | long | x10
INPUT_REGISTER | Read | 6337 |  | Solar | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 6338 |  | Solar Data | Hydraulic configuration |  |  |  |  | int
| Read |  | 0 | Solar | Option 1 active |  |  |  |  | bit
| Read |  | 1 | Solar | Option A active |  |  |  |  | bit
| Read |  | 2 | Solar | Option B active |  |  |  |  | bit
| Read |  | 3 | Solar | Option C active |  |  |  |  | bit
| Read |  | 4 | Solar | Option D active |  |  |  |  | bit
| Read |  | 5 | Solar | Option E active |  |  |  |  | bit
| Read |  | 6 | Solar | Option F active |  |  |  |  | bit
| Read |  | 7 | Solar | Option G active |  |  |  |  | bit
| Read |  | 8 | Solar | Option H active |  |  |  |  | bit
| Read |  | 9 | Solar | Option I active |  |  |  |  | bit
| Read |  | 10 | Solar | Option J active |  |  |  |  | bit
| Read |  | 11 | Solar | Option K active |  |  |  |  | bit
| Read |  | 12 | Solar | Option L active |  |  |  |  | bit
| Read |  | 13 | Solar | Option M active |  |  |  |  | bit
| Read |  | 14 | Solar | Option N active |  |  |  |  | bit
| Read |  | 15 | Solar | Option P active |  |  |  |  | bit
INPUT_REGISTER | Read | 6339 |  | Solar Data | irBitblock |  |  |  |  | int
| Read |  | 0 | Solar | Is Active |  |  |  |  | bit
INPUT_REGISTER |  | 6400 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 6401 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 6402 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 6403 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 6404 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 6405 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 6406 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 6407 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 6408 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 6409 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 6410 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 6411 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 6412 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 6413 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER | Read | 6422 |  | Energy Monitoring | Heat Output |  |  |  | kW | signed int | x10
INPUT_REGISTER | Read | 6423 |  | Energy Monitoring | Gas Consumption (LCV) |  |  |  | kW | signed int | x10
INPUT_REGISTER | Read | 6425 |  | Energy Monitoring | Electrical Power |  |  |  | W | int
INPUT_REGISTER | Read | 6430 |  | Fresh Water Characteristics 1 | DHW Out Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6431 |  | Fresh Water Characteristics 1 | DHW Volume Flow |  |  |  | L/min | signed int | x10
INPUT_REGISTER | Read | 6432 |  | Fresh Water Characteristics 1 | Prim In Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6433 |  | Fresh Water Characteristics 1 | DHW In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6434 |  | Fresh Water Characteristics 1 | Primary Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 6435 |  | Fresh Water Characteristics 1 | Request DHW Out Temperature |  |  |  | °C | int
INPUT_REGISTER | Read | 6436 |  | Fresh Water Characteristics 1 | Status Request DHW Out Temperature | 0 | 9 | 0-Off 1-DHWRed 2-DHW 3-Sol_red 4-Once_on 5-Therm_d 6-DlyHtUp 7-Preheat_start 8-Preheat_normal 9-No_eq |  | int
INPUT_REGISTER | Read | 6437 |  | Fresh Water Characteristics 2 | Circulation Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 6438 |  | Fresh Water Characteristics 2 | Status Circulation Pump | 0 | 8 | 0-Undefined 1-Test 2-BlckProt 3-No_req 4-AutoOff 5-AutoOn 6-Therm_d 7-Sys_Off 8-DlyHtUp |  | int
INPUT_REGISTER | Read | 6439 |  | Fresh Water Characteristics 2 | Return Valve Modulation Request |  |  |  | % | int
INPUT_REGISTER | Read | 6440 |  | Fresh Water Characteristics 2 | Valve State | 0 | 5 | 0-Undefined 1-TestMod 2-BlckProt 3-Mix_cl 4-Mix_opn 5-Sys_Off |  | int
INPUT_REGISTER | Read | 6441 |  | Fresh Water Characteristics 2 | Return Valve Buffer Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6442 |  | Fresh Water Characteristics 2 | Disinfection Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 6443 |  | Fresh Water Characteristics 2 | Pump State | 0 | 5 | 0-Undefined 1-TestMod 2-BlckPro 3-No_eq 4-Ht_req 5-Sys_Off |  | int
INPUT_REGISTER | Read | 6444 |  | Fresh Water Characteristics 1 | DHW Valve Power |  |  |  | % | int
INPUT_REGISTER | Read | 6445 |  | Fresh Water Characteristics 2 | Total Flow |  |  |  | L/min | int | x10
INPUT_REGISTER | Read | 6446 |  | Fresh Water 2 | Module 2 DHW Out Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6447 |  | Fresh Water 2 | Module 2 DHW Volume Flow |  |  |  | L/min | signed int | x10
INPUT_REGISTER | Read | 6448 |  | Fresh Water 2 | Module 2 Prim In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6449 |  | Fresh Water 2 | Module 2 DHW In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6450 |  | Fresh Water 2 | Module 2 DHW Valve Power |  |  |  | % | int
INPUT_REGISTER | Read | 6451 |  | Fresh Water 2 | Module 2 Prim Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 6452 |  | Fresh Water 2 | Module 2 Status Prim Pump |  |  |  |  | int
INPUT_REGISTER | Read | 6453 |  | Fresh Water 3 | Module 3 DHW Out Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6454 |  | Fresh Water 3 | Module 3 DHW Volume Flow |  |  |  | L/min | signed int | x10
INPUT_REGISTER | Read | 6455 |  | Fresh Water 3 | Module 3 Prim In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6456 |  | Fresh Water 3 | Module 3 DHW In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6457 |  | Fresh Water 3 | Module 3 DHW Valve Power |  |  |  | % | int
INPUT_REGISTER | Read | 6458 |  | Fresh Water 3 | Module 3 Prim Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 6459 |  | Fresh Water 3 | Module 3 Status Prim Pump |  |  |  |  | int
INPUT_REGISTER | Read | 6460 |  | Fresh Water 4 | Module 4 DHW Out Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6461 |  | Fresh Water 4 | Module 4 DHW Volume Flow |  |  |  | L/min | signed int | x10
INPUT_REGISTER | Read | 6462 |  | Fresh Water 4 | Module 4 Prim In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6463 |  | Fresh Water 4 | Module 4 DHW In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6464 |  | Fresh Water 4 | Module 4 DHW ValvePower |  |  |  | % | int
INPUT_REGISTER | Read | 6465 |  | Fresh Water 4 | Module 4 Prim Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 6466 |  | Fresh Water 4 | Module 4 Status Primary Pump |  |  |  |  | int
INPUT_REGISTER | Read | 6467 |  | Fresh Water | Fresh Water Hmi State |  |  |  |  | int
INPUT_REGISTER | Read | 6468 |  | Fresh Water Characteristics 3 | Fresh Water Configurations |  |  |  |  | int
| Read |  | 0 | Fresh Water | Option 2 active |  |  |  |  | bit
| Read |  | 1 | Fresh Water | Option A active |  |  |  |  | bit
| Read |  | 2 | Fresh Water | Option B active |  |  |  |  | bit
| Read |  | 3 | Fresh Water | Option C active |  |  |  |  | bit
| Read |  | 4 | Fresh Water | Option D active |  |  |  |  | bit
| Read |  | 5 | Fresh Water | Option E active |  |  |  |  | bit
| Read |  | 6 | Fresh Water | Option E active cascade module 2 active |  |  |  |  | bit
| Read |  | 7 | Fresh Water | Option E active cascade module 3 active |  |  |  |  | bit
| Read |  | 8 | Fresh Water | Option E active cascade module 4 active |  |  |  |  | bit
| Read |  | 9 | Fresh Water | Is Active |  |  |  |  | bit
INPUT_REGISTER | Read | 6476 |  | System | Error Key 1 |  |  |  |  | long
INPUT_REGISTER | Read | 6478 |  | System | Error Key 2 |  |  |  |  | long
INPUT_REGISTER | Read | 6480 |  | System | Error Key 3 |  |  |  |  | long
INPUT_REGISTER | Read | 6482 |  | System | Error Key 4 |  |  |  |  | long
INPUT_REGISTER | Read | 6484 |  | System | Error 1 Extra Info (MSB) |  |  |  |  | long
INPUT_REGISTER | Read | 6486 |  | System | Error 1 Extra Info (LSB) |  |  |  |  | long
INPUT_REGISTER | Read | 6488 |  | System | Error 2 Extra Info (MSB) |  |  |  |  | long
INPUT_REGISTER | Read | 6490 |  | System | Error 2 Extra Info (LSB) |  |  |  |  | long
INPUT_REGISTER | Read | 6492 |  | System | Error 3 Extra Info (MSB) |  |  |  |  | long
INPUT_REGISTER | Read | 6494 |  | System | Error 3 Extra Info (LSB) |  |  |  |  | long
INPUT_REGISTER | Read | 6496 |  | System | Error 4 Extra Info (MSB) |  |  |  |  | long
INPUT_REGISTER | Read | 6498 |  | System | Error 4 Extra Info (LSB) |  |  |  |  | long

## Slave13
Register Type | Permissions | Address | Bitblock Bit | Component | Name | Min | Max | Range | Unit | DataType | Float to Int Factor
HOLDING_REGISTER | Write | 6507 |  | DomesticHotWater Zm/Ems | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 6508 |  | DomesticHotWater Zm/Ems | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 6509 |  | DomesticHotWater Zm/Ems | Thermal Disinfection Setpoint | 65 | 75 |  | °C | int | x10
HOLDING_REGISTER | Write | 6510 |  | DomesticHotWater Zm | Setpoint Auto Day | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 6511 |  | DomesticHotWater Zm | Setpoint Auto Night | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 6512 |  | DomesticHotWater Zm | Setpoint Manual Day | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 6513 |  | DomesticHotWater Zm | Setpoint Manual Night | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 6514 |  | DomesticHotWater Zm | Setpoint Holiday | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 6515 |  | DomesticHotWater Zm/Ems | Circulation Pump Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 6516 |  | DomesticHotWater Zm/Ems | Circulation Pump Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 6517 |  | DomesticHotWater Zm/Ems | Disinfection Frequency | 0 | 7 | 0-Daily 1-Monday 2-Tuesday 3-Wednesday 4-Thursday 5-Friday 6-Saturday 7-Sunday |  | int
HOLDING_REGISTER | Write | 6518 |  | DomesticHotWater Zm/Ems | Disinfection Start Hour | 0 | 23 |  | h | int
HOLDING_REGISTER | Write | 6521 |  | DomesticHotWater Fm | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 6522 |  | DomesticHotWater Fm | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 6523 |  | DomesticHotWater Fm | Thermal Disinfection Setpoint | 65 | 75 |  | °C | int | x10
HOLDING_REGISTER | Write | 6524 |  | DomesticHotWater Fm | Setpoint Auto Day | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 6525 |  | DomesticHotWater Fm | Setpoint Auto Night | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 6526 |  | DomesticHotWater Fm | Setpoint Manual Day | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 6527 |  | DomesticHotWater Fm | Setpoint Manual Night | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 6528 |  | DomesticHotWater Fm | Setpoint Holiday | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 6529 |  | DomesticHotWater Fm | Circulation Pump Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 6530 |  | DomesticHotWater Fm | Circulation Pump Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 6531 |  | DomesticHotWater Fm | Disinfection Frequency | 0 | 7 | 0-Daily 1-Monday 2-Tuesday 3-Wednesday 4-Thursday 5-Friday 6-Saturday 7-Sunday |  | int
HOLDING_REGISTER | Write | 6532 |  | DomesticHotWater Fm | Disinfection Start Hour | 0 | 23 |  | h | int
HOLDING_REGISTER | Read | 6539 |  | Boiler | Control Type | 0 | 4 | 0-None 1-Safe 2-Ems 3-7Pole 4-Substation |  | int
HOLDING_REGISTER | Write | 6543 |  | AlternativeHeatSource | Operation Mode Request Auto Day | 20 | 99 |  | °C | int
HOLDING_REGISTER | Write | 6544 |  | AlternativeHeatSource | Operation Mode Request Auto Night | 20 | 99 |  | °C | int
HOLDING_REGISTER | Write | 6545 |  | AlternativeHeatSource | Operation Mode Request Manual Day | 20 | 99 |  | °C | int
HOLDING_REGISTER | Write | 6546 |  | AlternativeHeatSource | Operation Mode Request Manual Night | 20 | 99 |  | °C | int
HOLDING_REGISTER | Write | 6547 |  | AlternativeHeatSource | Operation Mode Request Holiday | 20 | 99 |  | °C | int
HOLDING_REGISTER | Write | 6548 |  | AlternativeHeatSource | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 6549 |  | AlternativeHeatSource | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 6550 |  | AlternativeHeatSource | Return Control Setpoint User | 10 | 70 |  | °C | int
HOLDING_REGISTER | Write | 6557 |  | HydraulicCircuit Zm | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 6558 |  | HydraulicCircuit Zm | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 6559 |  | HydraulicCircuit Zm | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6560 |  | HydraulicCircuit Zm | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6561 |  | HydraulicCircuit Zm | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6562 |  | HydraulicCircuit Zm | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6563 |  | HydraulicCircuit Zm | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6564 |  | HydraulicCircuit Zm | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 6570 |  | HydraulicCircuit 1 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 6571 |  | HydraulicCircuit 1 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 6572 |  | HydraulicCircuit 1 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6573 |  | HydraulicCircuit 1 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6574 |  | HydraulicCircuit 1 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6575 |  | HydraulicCircuit 1 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6576 |  | HydraulicCircuit 1 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6577 |  | HydraulicCircuit 1 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 6583 |  | HydraulicCircuit 2 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 6584 |  | HydraulicCircuit 2 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 6585 |  | HydraulicCircuit 2 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6586 |  | HydraulicCircuit 2 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6587 |  | HydraulicCircuit 2 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6588 |  | HydraulicCircuit 2 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6589 |  | HydraulicCircuit 2 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6590 |  | HydraulicCircuit 2 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 6596 |  | HydraulicCircuit 3 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 6597 |  | HydraulicCircuit 3 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 6598 |  | HydraulicCircuit 3 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6599 |  | HydraulicCircuit 3 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6600 |  | HydraulicCircuit 3 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6601 |  | HydraulicCircuit 3 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6602 |  | HydraulicCircuit 3 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6603 |  | HydraulicCircuit 3 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 6609 |  | HydraulicCircuit 4 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 6610 |  | HydraulicCircuit 4 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 6611 |  | HydraulicCircuit 4 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6612 |  | HydraulicCircuit 4 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6613 |  | HydraulicCircuit 4 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6614 |  | HydraulicCircuit 4 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6615 |  | HydraulicCircuit 4 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6616 |  | HydraulicCircuit 4 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 6622 |  | HydraulicCircuit 5 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 6623 |  | HydraulicCircuit 5 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 6624 |  | HydraulicCircuit 5 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6625 |  | HydraulicCircuit 5 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6626 |  | HydraulicCircuit 5 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6627 |  | HydraulicCircuit 5 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6628 |  | HydraulicCircuit 5 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6629 |  | HydraulicCircuit 5 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 6635 |  | HydraulicCircuit 6 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 6636 |  | HydraulicCircuit 6 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 6637 |  | HydraulicCircuit 6 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6638 |  | HydraulicCircuit 6 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6639 |  | HydraulicCircuit 6 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6640 |  | HydraulicCircuit 6 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6641 |  | HydraulicCircuit 6 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6642 |  | HydraulicCircuit 6 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 6648 |  | HydraulicCircuit 7 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 6649 |  | HydraulicCircuit 7 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 6650 |  | HydraulicCircuit 7 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6651 |  | HydraulicCircuit 7 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6652 |  | HydraulicCircuit 7 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6653 |  | HydraulicCircuit 7 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6654 |  | HydraulicCircuit 7 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6655 |  | HydraulicCircuit 7 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 6661 |  | HydraulicCircuit 8 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 6662 |  | HydraulicCircuit 8 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 6663 |  | HydraulicCircuit 8 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6664 |  | HydraulicCircuit 8 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6665 |  | HydraulicCircuit 8 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6666 |  | HydraulicCircuit 8 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6667 |  | HydraulicCircuit 8 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 6668 |  | HydraulicCircuit 8 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 6701 |  | Heat Pump | Heat demand source | 0 | 2 | 0-Scheduler 1-System 2-Max_system_scheduler |  | int
HOLDING_REGISTER | Read | 6921 |  | Fresh Water Characteristics 3 | DHU Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 6922 |  | Fresh Water Characteristics 3 | Extra Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 6923 |  | Fresh Water Characteristics 3 | Maximum DHW Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 6924 |  | Fresh Water Characteristics 3 | On High Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 6925 |  | Fresh Water Characteristics 3 | On Low Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 6926 |  | Fresh Water Characteristics 3 | Fresh Water Type | 0 | 3 | 0-15/20l/min 1-27l/min 2-40l/min 3-60l/min |  | int
HOLDING_REGISTER | Read | 6927 |  | Fresh Water Characteristics 3 | Enable Alarm Output | 0 | 2 | 0-No 1-Yes 2-Inverted |  | int
HOLDING_REGISTER | Read | 6928 |  | Fresh Water Characteristics 3 | Buffer Cylinder Temperature Offset |  |  |  | K | int
HOLDING_REGISTER | Read | 6929 |  | Fresh Water Characteristics 3 | hrBitblock |  |  |  |  | int
| Read |  | 0 | Fresh Water | Buffer Cylinder Temperature Optimization Enabled |  |  |  |  | bit
| Read |  | 1 | Fresh Water | Impulse Enabled |  |  |  |  | bit
| Read |  | 2 | Fresh Water | Time Program Enabled |  |  |  |  | bit
HOLDING_REGISTER | Read | 6930 |  | Fresh Water Characteristics 3 | Minimum Buffer Cylinder Temperature Offset |  |  |  | K | int
HOLDING_REGISTER | Read | 6931 |  | Fresh Water Characteristics 2 | Circulation Pump Runs per Hour | 0 | 7 | 0-Undefined 1-1x3_minutes/h 2-2x3_minutes/h 3-3x3_minutes/h 4-4x3_minutes/h 5-5x3_minutes/h 6-6x3_minutes/h 7-Permanent |  | int
HOLDING_REGISTER | Read | 6932 |  | Fresh Water Characteristics 2 | Swich Hysteresis |  |  |  | K | int
HOLDING_REGISTER | Read | 6933 |  | Fresh Water Characteristics 2 | Thermal Disinfection Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 6934 |  | Fresh Water Characteristics 2 | Pre Heat Maximum Temperature |  |  |  | °C | int
INPUT_REGISTER | Read | 6500 |  | System | Own Outdoor temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6501 |  | System | Damped Own outdoor temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6504 |  | System | Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6508 |  | System | Active Functions 1 |  |  |  |  | int
INPUT_REGISTER | Read | 6509 |  | System | Active Functions 2 |  |  |  |  | int
INPUT_REGISTER | Read | 6515 |  | DomesticHotWater Zm | Charge Pump Running | 0 | 4 | 0-Stopping 1-Starting 2-Running 3-Off 4-Error |  | int
INPUT_REGISTER | Read | 6516 |  | DomesticHotWater Zm | Circulation Pump Running | 0 | 4 | 0-Stopping 1-Starting 2-Running 3-Off 4-Error |  | int
INPUT_REGISTER | Read | 6517 |  | DomesticHotWater Zm | Hydraulic State | 0 | 7 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Cold_load 6-Post_purge 7-Condense_protection |  | int
INPUT_REGISTER | Read | 6518 |  | DomesticHotWater Zm/Ems | Thermal Disinfection Status | 0 | 3 | 0-Off 1-On 2-Success 3-Error |  | int
INPUT_REGISTER | Read | 6519 |  | DomesticHotWater Zm/Ems | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 6520 |  | DomesticHotWater Zm/Ems | Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6521 |  | DomesticHotWater Zm/Ems | Current Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6531 |  | DomesticHotWater Fm | Charge Pump Running | 0 | 4 | 0-Stopping 1-Starting 2-Running 3-Off 4-Error |  | int
INPUT_REGISTER | Read | 6532 |  | DomesticHotWater Fm | Circulation Pump Running | 0 | 4 | 0-Stopping 1-Starting 2-Running 3-Off 4-Error |  | int
INPUT_REGISTER | Read | 6533 |  | DomesticHotWater Fm | Hydraulic State | 0 | 7 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Cold_load 6-Post_purge 7-Condense_protection |  | int
INPUT_REGISTER | Read | 6534 |  | DomesticHotWater Fm | Thermal Disinfection Status | 0 | 3 | 0-Off 1-On 2-Success 3-Error |  | int
INPUT_REGISTER | Read | 6535 |  | DomesticHotWater Fm | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 6536 |  | DomesticHotWater Fm | Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6537 |  | DomesticHotWater Fm | Current Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER |  | 6547 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 6548 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 6550 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 6552 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 6553 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 6554 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 6555 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 6556 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 6559 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 6560 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER | Read | 6563 |  | AlternativeHeatSource | Operating hours |  |  |  | h | long
INPUT_REGISTER | Read | 6565 |  | AlternativeHeatSource | Heat Source Starts |  |  |  |  | long
INPUT_REGISTER | Read | 6567 |  | AlternativeHeatSource | Heat Source Hours to Maintenance |  |  |  | h | int
INPUT_REGISTER | Read | 6569 |  | AlternativeHeatSource | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
| Read |  | 0 | AlternativeHeatSource | Is Heat Source On |  |  |  |  | bit
| Read |  | 1 | AlternativeHeatSource | Is Heat Source On Request |  |  |  |  | bit
INPUT_REGISTER | Read | 6587 |  | HydraulicCircuit Zm | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6588 |  | HydraulicCircuit Zm | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6589 |  | HydraulicCircuit Zm | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6590 |  | HydraulicCircuit Zm | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6591 |  | HydraulicCircuit Zm | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 6592 |  | HydraulicCircuit Zm | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 6593 |  | HydraulicCircuit Zm | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 6594 |  | HydraulicCircuit Zm | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 6595 |  | HydraulicCircuit Zm | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 6599 |  | HydraulicCircuit 1 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6600 |  | HydraulicCircuit 1 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6601 |  | HydraulicCircuit 1 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6602 |  | HydraulicCircuit 1 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6603 |  | HydraulicCircuit 1 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 6604 |  | HydraulicCircuit 1 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 6605 |  | HydraulicCircuit 1 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 6606 |  | HydraulicCircuit 1 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 6607 |  | HydraulicCircuit 1 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 6612 |  | HydraulicCircuit 2 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6613 |  | HydraulicCircuit 2 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6614 |  | HydraulicCircuit 2 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6615 |  | HydraulicCircuit 2 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6616 |  | HydraulicCircuit 2 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 6617 |  | HydraulicCircuit 2 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 6618 |  | HydraulicCircuit 2 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 6619 |  | HydraulicCircuit 2 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 6620 |  | HydraulicCircuit 2 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 6625 |  | HydraulicCircuit 3 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6626 |  | HydraulicCircuit 3 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6627 |  | HydraulicCircuit 3 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6628 |  | HydraulicCircuit 3 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6629 |  | HydraulicCircuit 3 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 6630 |  | HydraulicCircuit 3 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 6631 |  | HydraulicCircuit 3 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 6632 |  | HydraulicCircuit 3 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 6633 |  | HydraulicCircuit 3 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 6638 |  | HydraulicCircuit 4 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6639 |  | HydraulicCircuit 4 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6640 |  | HydraulicCircuit 4 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6641 |  | HydraulicCircuit 4 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6642 |  | HydraulicCircuit 4 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 6643 |  | HydraulicCircuit 4 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 6644 |  | HydraulicCircuit 4 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 6645 |  | HydraulicCircuit 4 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 6646 |  | HydraulicCircuit 4 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 6651 |  | HydraulicCircuit 5 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6652 |  | HydraulicCircuit 5 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6653 |  | HydraulicCircuit 5 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6654 |  | HydraulicCircuit 5 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6655 |  | HydraulicCircuit 5 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 6656 |  | HydraulicCircuit 5 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 6657 |  | HydraulicCircuit 5 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 6658 |  | HydraulicCircuit 5 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 6659 |  | HydraulicCircuit 5 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 6664 |  | HydraulicCircuit 6 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6665 |  | HydraulicCircuit 6 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6666 |  | HydraulicCircuit 6 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6667 |  | HydraulicCircuit 6 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6668 |  | HydraulicCircuit 6 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 6669 |  | HydraulicCircuit 6 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 6670 |  | HydraulicCircuit 6 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 6671 |  | HydraulicCircuit 6 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 6672 |  | HydraulicCircuit 6 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 6677 |  | HydraulicCircuit 7 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6678 |  | HydraulicCircuit 7 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6679 |  | HydraulicCircuit 7 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6680 |  | HydraulicCircuit 7 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6681 |  | HydraulicCircuit 7 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 6682 |  | HydraulicCircuit 7 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 6683 |  | HydraulicCircuit 7 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 6684 |  | HydraulicCircuit 7 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 6685 |  | HydraulicCircuit 7 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 6690 |  | HydraulicCircuit 8 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6691 |  | HydraulicCircuit 8 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6692 |  | HydraulicCircuit 8 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6693 |  | HydraulicCircuit 8 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6694 |  | HydraulicCircuit 8 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 6695 |  | HydraulicCircuit 8 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 6696 |  | HydraulicCircuit 8 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 6697 |  | HydraulicCircuit 8 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 6698 |  | HydraulicCircuit 8 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 6703 |  | i2c | Global Error State | 0 | 4 | 0-No_Error 1-i2c_driver_error 2-Wrong_Cycle_Time 3-Missing_Module_Slot 4-Module_Slot_Error |  | int
INPUT_REGISTER | Read | 6704 |  | i2c | Slot1 Module Detected |  |  | 0-Unknown 1-None 22-FM_CM 25-FM_SI 28-FM_MM 29-FM_MW 30-FM_AM 31-FM_CM2 |  | int
INPUT_REGISTER | Read | 6705 |  | i2c | Slot1 Error State |  |  | 0-No_Error 1-No_Response 2-Wrong_Module 3-Unsupported_Module 4-Internal_Sw_Error 5-Communication_Failed 6-Internal_Module_Error 7-Module_Not_Supported_Current_Variant 8-Module_Not_Suppported_In_Slot 9-Module_Count_Too_High 10-Module_Not_Supported_With_Connected_Boiler_Type |  | int
INPUT_REGISTER | Read | 6706 |  | i2c | Slot2 Module Detected |  |  | 0-Unknown 1-None 22-FM_CM 25-FM_SI 28-FM_MM 29-FM_MW 30-FM_AM 31-FM_CM2 |  | int
INPUT_REGISTER | Read | 6707 |  | i2c | Slot2 Error State |  |  | 0-No_Error 1-No_Response 2-Wrong_Module 3-Unsupported_Module 4-Internal_Sw_Error 5-Communication_Failed 6-Internal_Module_Error 7-Module_Not_Supported_Current_Variant 8-Module_Not_Suppported_In_Slot 9-Module_Count_Too_High 10-Module_Not_Supported_With_Connected_Boiler_Type |  | int
INPUT_REGISTER | Read | 6708 |  | i2c | Slot3 Module Detected |  |  | 0-Unknown 1-None 22-FM_CM 25-FM_SI 28-FM_MM 29-FM_MW 30-FM_AM 31-FM_CM2 |  | int
INPUT_REGISTER | Read | 6709 |  | i2c | Slot3 Error State |  |  | 0-No_Error 1-No_Response 2-Wrong_Module 3-Unsupported_Module 4-Internal_Sw_Error 5-Communication_Failed 6-Internal_Module_Error 7-Module_Not_Supported_Current_Variant 8-Module_Not_Suppported_In_Slot 9-Module_Count_Too_High 10-Module_Not_Supported_With_Connected_Boiler_Type |  | int
INPUT_REGISTER | Read | 6710 |  | i2c | Slot4 Module Detected |  |  | 0-Unknown 1-None 22-FM_CM 25-FM_SI 28-FM_MM 29-FM_MW 30-FM_AM 31-FM_CM2 |  | int
INPUT_REGISTER | Read | 6711 |  | i2c | Slot4 Error State |  |  | 0-No_Error 1-No_Response 2-Wrong_Module 3-Unsupported_Module 4-Internal_Sw_Error 5-Communication_Failed 6-Internal_Module_Error 7-Module_Not_Supported_Current_Variant 8-Module_Not_Suppported_In_Slot 9-Module_Count_Too_High 10-Module_Not_Supported_With_Connected_Boiler_Type |  | int
INPUT_REGISTER | Read | 6712 |  | i2c | Slot A Module Detected |  |  | 0-Unknown 1-None 26-ZM5313 27-ZM5311 |  | int
INPUT_REGISTER | Read | 6713 |  | i2c | Slot A Error State |  |  | 0-No_Error 1-No_Response 2-Wrong_Module 3-Unsupported_Module 4-Internal_Sw_Error 5-Communication_Failed 6-Internal_Module_Error 7-Module_Not_Supported_Current_Variant 8-Module_Not_Suppported_In_Slot 9-Module_Count_Too_High 10-Module_Not_Supported_With_Connected_Boiler_Type |  | int
INPUT_REGISTER | Read | 6714 |  | i2c | irBitblock |  |  |  |  | int
| Read |  | 0 | i2c | Component Error |  |  |  |  | bit
INPUT_REGISTER | Read | 6725 |  | fm-si | irBitblock |  |  |  |  | int
| Read |  | 0 | fm-si | Input 1 Error |  |  |  |  | bit
| Read |  | 1 | fm-si | Input 2 Error |  |  |  |  | bit
| Read |  | 2 | fm-si | Input 3 Error |  |  |  |  | bit
| Read |  | 3 | fm-si | Input 4 Error |  |  |  |  | bit
| Read |  | 4 | fm-si | Input 5 Error |  |  |  |  | bit
INPUT_REGISTER | Read | 6732 |  | Sdc | Demand Mode (Low Priority) | 0 | 2 | 0-Off 1-Take_Heat 2-Give_Heat |  | int
INPUT_REGISTER | Read | 6733 |  | Sdc | Demand Flow Temp (Low Priority) |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6734 |  | Sdc | Demand Mode (High Priority) | 0 | 2 | 0-Off 1-Take_Heat 2-Give_Heat |  | int
INPUT_REGISTER | Read | 6735 |  | Sdc | Demand Flow Temp (High Priority) |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6739 |  | Heat Pump | System return temperature for HP heating buffer |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6740 |  | Heat Pump | Buffer mid temperature for HP heating buffer |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6741 |  | Heat Pump | Buffer top temperature for HP heating buffer |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6742 |  | Heat Pump | Buffer bottom temperature for HP heating buffer |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6743 |  | Heat Pump | Return temperature FWR |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6744 |  | Heat Pump | Flow temperature FWV |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6745 |  | Heat Pump | Flow temperature HP |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6746 |  | Heat Pump | Return temperature HP |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6747 |  | Heat Pump | HMI State of HP Component | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 6748 |  | Heat Pump | HP current heat output |  |  |  | kW | signed int | x10
INPUT_REGISTER | Read | 6749 |  | Heat Pump | HP current electrical power consumption | 0 | 10000 |  | kW | int | x10
INPUT_REGISTER | Read | 6750 |  | Heat Pump | HP Smart grid mode | 0 | 3 | 0-normal_charging_grid 1-low_charging_grid 2-high_charging_grid 3-free_charging_grid |  | int
INPUT_REGISTER | Read | 6751 |  | Heat Pump | Heat demand temperature set point |  |  |  | °C | int
INPUT_REGISTER | Read | 6752 |  | Heat Pump | heatPumpStatusIrBitblock | 0 |  |  |  | int
INPUT_REGISTER | Read | 6753 |  | Heat Pump | Ambient Temperature HP |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6754 |  | Heat Pump | HP silent mode | 0 | 3 | 0-standard_mode 1-silent_mode 2-super_silent_mode 3-night_mode |  | int
INPUT_REGISTER | Read | 6755 |  | Heat Pump | Heat Pump Heat Request Temperature |  |  |  | °C | int
INPUT_REGISTER | Read | 6756 |  | Heat Pump | heatPumpIrBitblock |  |  |  |  | int
INPUT_REGISTER | Read | 6765 |  | System | Open Notifications Count |  |  |  |  | int
INPUT_REGISTER | Read | 6766 |  | System | Error Key 5 |  |  |  |  | long
INPUT_REGISTER | Read | 6768 |  | System | Error Key 6 |  |  |  |  | long
INPUT_REGISTER | Read | 6770 |  | System | Error Key 7 |  |  |  |  | long
INPUT_REGISTER | Read | 6772 |  | System | Error Key 8 |  |  |  |  | long
INPUT_REGISTER | Read | 6774 |  | System | Error Key 9 |  |  |  |  | long
INPUT_REGISTER | Read | 6776 |  | System | Error Key 10 |  |  |  |  | long
INPUT_REGISTER | Read | 6778 |  | Chp / EC Power | Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6779 |  | Chp / EC Power | Return Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6780 |  | Chp | Flue Gas Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6781 |  | Chp | Motor Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6782 |  | Chp / EC Power | Current Generator Power |  |  |  | kW | int
INPUT_REGISTER | Read | 6783 |  | Chp | Current Power Setpoint |  |  |  | kW | int
INPUT_REGISTER | Read | 6784 |  | Chp / EC Power | Operation Hours |  |  |  | h | long
INPUT_REGISTER | Read | 6786 |  | Chp / EC Power | Number of starts |  |  |  |  | long
INPUT_REGISTER | Read | 6788 |  | Chp / EC Power | Hours to Maintenance |  |  |  | h | int
INPUT_REGISTER | Read | 6790 |  | Chp | Output Power Setpoint |  |  |  | kW | int
INPUT_REGISTER | Read | 6791 |  | Chp | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 6796 |  | Chp | irBitblock |  |  |  |  | int
| Read |  | 0 | Chp | Warning |  |  |  |  | bit
| Read |  | 1 | Chp / EC Power | Malfunction |  |  |  |  | bit
| Read |  | 2 | Chp / EC Power | Controlled Shutdown |  |  |  |  | bit
| Read |  | 3 | Chp / EC Power | Generator On |  |  |  |  | bit
| Read |  | 4 | Chp | Automatic On |  |  |  |  | bit
| Read |  | 5 | Chp / EC Power | Automatic Ready |  |  |  |  | bit
| Read |  | 11 | Chp / EC Power | Output On Request |  |  |  |  | bit
INPUT_REGISTER | Read | 6804 |  | Water Treatment Module | Program Step |  |  | 20-140: Desalination not active 10000-10810: One time desalination 20000-20810: Automatic desalination 30000-30260: Stationary operation |  | int
INPUT_REGISTER | Read | 6805 |  | Water Treatment Module | Temperature Desalinization |  |  |  | °C | int | x10
INPUT_REGISTER | Read | 6806 |  | Water Treatment Module | Volume Flow |  |  |  | L/min | int | x10
INPUT_REGISTER | Read | 6807 |  | Water Treatment Module | Conductivity system |  |  |  | uS/cm | int | x10
INPUT_REGISTER | Read | 6808 |  | Water Treatment Module | Conductivity cartridge |  |  |  | uS/cm | int | x10
INPUT_REGISTER | Read | 6809 |  | Water Treatment Module | Cartridge Capacity |  |  |  | % | int
INPUT_REGISTER | Read | 6813 |  | Solar Data | Collector temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6814 |  | Solar Data | Temperature cylinder bottom |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6815 |  | Solar Data | Solar pump modulation setpoint |  |  |  | % | int
INPUT_REGISTER | Read | 6816 |  | Solar | Solar pump status | 0 | 19 | 1-TestMod 2-BlckProt 3-No heat 4-Ht avail 5-SolOff 6-MaxCyl 7-MaxColl 8-MinColl 9-FrostP 10-VacFct 11-SwChck 12-MixPrio 13-Switch 14-Priority 15-ThermD 16-MixCal 17-MixOpn 18-MixCl 19-MixOff |  | int
INPUT_REGISTER | Read | 6817 |  | Solar Data | Heat exchanger temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6818 |  | Solar Data | Heat exchanger pump modulation setpoint |  |  |  | % | int
INPUT_REGISTER | Read | 6819 |  | Solar | Heat exchanger pump status | 0 | 19 | 1-TestMod 2-BlckProt 3-No heat 4-Ht avail 5-SolOff 6-MaxCyl 7-MaxColl 8-MinColl 9-FrostP 10-VacFct 11-SwChck 12-MixPrio 13-Switch 14-Priority 15-ThermD 16-MixCal 17-MixOpn 18-MixCl 19-MixOff |  | int
INPUT_REGISTER | Read | 6820 |  | Solar Data | Temperature cylinder 3 top |  |  |  | °C | int | x10
INPUT_REGISTER | Read | 6821 |  | Solar Data | Reload pump modulation setpoint |  |  |  | % | int
INPUT_REGISTER | Read | 6822 |  | Solar | Reload pump status | 0 | 19 | 1-TestMod 2-BlckProt 3-No heat 4-Ht avail 5-SolOff 6-MaxCyl 7-MaxColl 8-MinColl 9-FrostP 10-VacFct 11-SwChck 12-MixPrio 13-Switch 14-Priority 15-ThermD 16-MixCal 17-MixOpn 18-MixCl 19-MixOff |  | int
INPUT_REGISTER | Read | 6823 |  | Solar | Pump therm. disinfect. status | 0 | 19 | 1-TestMod 2-BlckProt 3-No heat 4-Ht avail 5-SolOff 6-MaxCyl 7-MaxColl 8-MinColl 9-FrostP 10-VacFct 11-SwChck 12-MixPrio 13-Switch 14-Priority 15-ThermD 16-MixCal 17-MixOpn 18-MixCl 19-MixOff |  | int
INPUT_REGISTER | Read | 6824 |  | Solar Yield | Flow temperature heat meter |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6825 |  | Solar Yield | Return temperature heat meter |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6826 |  | Solar Yield | Heat count pulse counter | 0 | 15 |  |  | int
INPUT_REGISTER | Read | 6827 |  | Solar Yield | Solar yield per month |  |  |  | kWh | long | x10
INPUT_REGISTER | Read | 6829 |  | Solar Yield | Solar yield per year |  |  |  | kWh | long | x10
INPUT_REGISTER | Read | 6831 |  | Solar Yield | Last hour solar yield |  |  |  | kWh | long | x10
INPUT_REGISTER | Read | 6833 |  | Solar Yield | Solar yield per day |  |  |  | kWh | long | x10
INPUT_REGISTER | Read | 6835 |  | Solar Yield | Solar yield since installation |  |  |  | kWh | long | x10
INPUT_REGISTER | Read | 6837 |  | Solar | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 6838 |  | Solar Data | Hydraulic configuration |  |  |  |  | int
| Read |  | 0 | Solar | Option 1 active |  |  |  |  | bit
| Read |  | 1 | Solar | Option A active |  |  |  |  | bit
| Read |  | 2 | Solar | Option B active |  |  |  |  | bit
| Read |  | 3 | Solar | Option C active |  |  |  |  | bit
| Read |  | 4 | Solar | Option D active |  |  |  |  | bit
| Read |  | 5 | Solar | Option E active |  |  |  |  | bit
| Read |  | 6 | Solar | Option F active |  |  |  |  | bit
| Read |  | 7 | Solar | Option G active |  |  |  |  | bit
| Read |  | 8 | Solar | Option H active |  |  |  |  | bit
| Read |  | 9 | Solar | Option I active |  |  |  |  | bit
| Read |  | 10 | Solar | Option J active |  |  |  |  | bit
| Read |  | 11 | Solar | Option K active |  |  |  |  | bit
| Read |  | 12 | Solar | Option L active |  |  |  |  | bit
| Read |  | 13 | Solar | Option M active |  |  |  |  | bit
| Read |  | 14 | Solar | Option N active |  |  |  |  | bit
| Read |  | 15 | Solar | Option P active |  |  |  |  | bit
INPUT_REGISTER | Read | 6839 |  | Solar Data | irBitblock |  |  |  |  | int
| Read |  | 0 | Solar | Is Active |  |  |  |  | bit
INPUT_REGISTER |  | 6900 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 6901 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 6902 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 6903 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 6904 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 6905 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 6906 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 6907 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 6908 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 6909 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 6910 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 6911 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 6912 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 6913 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER | Read | 6922 |  | Energy Monitoring | Heat Output |  |  |  | kW | signed int | x10
INPUT_REGISTER | Read | 6923 |  | Energy Monitoring | Gas Consumption (LCV) |  |  |  | kW | signed int | x10
INPUT_REGISTER | Read | 6925 |  | Energy Monitoring | Electrical Power |  |  |  | W | int
INPUT_REGISTER | Read | 6930 |  | Fresh Water Characteristics 1 | DHW Out Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6931 |  | Fresh Water Characteristics 1 | DHW Volume Flow |  |  |  | L/min | signed int | x10
INPUT_REGISTER | Read | 6932 |  | Fresh Water Characteristics 1 | Prim In Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6933 |  | Fresh Water Characteristics 1 | DHW In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6934 |  | Fresh Water Characteristics 1 | Primary Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 6935 |  | Fresh Water Characteristics 1 | Request DHW Out Temperature |  |  |  | °C | int
INPUT_REGISTER | Read | 6936 |  | Fresh Water Characteristics 1 | Status Request DHW Out Temperature | 0 | 9 | 0-Off 1-DHWRed 2-DHW 3-Sol_red 4-Once_on 5-Therm_d 6-DlyHtUp 7-Preheat_start 8-Preheat_normal 9-No_eq |  | int
INPUT_REGISTER | Read | 6937 |  | Fresh Water Characteristics 2 | Circulation Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 6938 |  | Fresh Water Characteristics 2 | Status Circulation Pump | 0 | 8 | 0-Undefined 1-Test 2-BlckProt 3-No_req 4-AutoOff 5-AutoOn 6-Therm_d 7-Sys_Off 8-DlyHtUp |  | int
INPUT_REGISTER | Read | 6939 |  | Fresh Water Characteristics 2 | Return Valve Modulation Request |  |  |  | % | int
INPUT_REGISTER | Read | 6940 |  | Fresh Water Characteristics 2 | Valve State | 0 | 5 | 0-Undefined 1-TestMod 2-BlckProt 3-Mix_cl 4-Mix_opn 5-Sys_Off |  | int
INPUT_REGISTER | Read | 6941 |  | Fresh Water Characteristics 2 | Return Valve Buffer Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6942 |  | Fresh Water Characteristics 2 | Disinfection Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 6943 |  | Fresh Water Characteristics 2 | Pump State | 0 | 5 | 0-Undefined 1-TestMod 2-BlckPro 3-No_eq 4-Ht_req 5-Sys_Off |  | int
INPUT_REGISTER | Read | 6944 |  | Fresh Water Characteristics 1 | DHW Valve Power |  |  |  | % | int
INPUT_REGISTER | Read | 6945 |  | Fresh Water Characteristics 2 | Total Flow |  |  |  | L/min | int | x10
INPUT_REGISTER | Read | 6946 |  | Fresh Water 2 | Module 2 DHW Out Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6947 |  | Fresh Water 2 | Module 2 DHW Volume Flow |  |  |  | L/min | signed int | x10
INPUT_REGISTER | Read | 6948 |  | Fresh Water 2 | Module 2 Prim In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6949 |  | Fresh Water 2 | Module 2 DHW In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6950 |  | Fresh Water 2 | Module 2 DHW Valve Power |  |  |  | % | int
INPUT_REGISTER | Read | 6951 |  | Fresh Water 2 | Module 2 Prim Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 6952 |  | Fresh Water 2 | Module 2 Status Prim Pump |  |  |  |  | int
INPUT_REGISTER | Read | 6953 |  | Fresh Water 3 | Module 3 DHW Out Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6954 |  | Fresh Water 3 | Module 3 DHW Volume Flow |  |  |  | L/min | signed int | x10
INPUT_REGISTER | Read | 6955 |  | Fresh Water 3 | Module 3 Prim In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6956 |  | Fresh Water 3 | Module 3 DHW In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6957 |  | Fresh Water 3 | Module 3 DHW Valve Power |  |  |  | % | int
INPUT_REGISTER | Read | 6958 |  | Fresh Water 3 | Module 3 Prim Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 6959 |  | Fresh Water 3 | Module 3 Status Prim Pump |  |  |  |  | int
INPUT_REGISTER | Read | 6960 |  | Fresh Water 4 | Module 4 DHW Out Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6961 |  | Fresh Water 4 | Module 4 DHW Volume Flow |  |  |  | L/min | signed int | x10
INPUT_REGISTER | Read | 6962 |  | Fresh Water 4 | Module 4 Prim In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6963 |  | Fresh Water 4 | Module 4 DHW In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 6964 |  | Fresh Water 4 | Module 4 DHW ValvePower |  |  |  | % | int
INPUT_REGISTER | Read | 6965 |  | Fresh Water 4 | Module 4 Prim Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 6966 |  | Fresh Water 4 | Module 4 Status Primary Pump |  |  |  |  | int
INPUT_REGISTER | Read | 6967 |  | Fresh Water | Fresh Water Hmi State |  |  |  |  | int
INPUT_REGISTER | Read | 6968 |  | Fresh Water Characteristics 3 | Fresh Water Configurations |  |  |  |  | int
| Read |  | 0 | Fresh Water | Option 2 active |  |  |  |  | bit
| Read |  | 1 | Fresh Water | Option A active |  |  |  |  | bit
| Read |  | 2 | Fresh Water | Option B active |  |  |  |  | bit
| Read |  | 3 | Fresh Water | Option C active |  |  |  |  | bit
| Read |  | 4 | Fresh Water | Option D active |  |  |  |  | bit
| Read |  | 5 | Fresh Water | Option E active |  |  |  |  | bit
| Read |  | 6 | Fresh Water | Option E active cascade module 2 active |  |  |  |  | bit
| Read |  | 7 | Fresh Water | Option E active cascade module 3 active |  |  |  |  | bit
| Read |  | 8 | Fresh Water | Option E active cascade module 4 active |  |  |  |  | bit
| Read |  | 9 | Fresh Water | Is Active |  |  |  |  | bit
INPUT_REGISTER | Read | 6976 |  | System | Error Key 1 |  |  |  |  | long
INPUT_REGISTER | Read | 6978 |  | System | Error Key 2 |  |  |  |  | long
INPUT_REGISTER | Read | 6980 |  | System | Error Key 3 |  |  |  |  | long
INPUT_REGISTER | Read | 6982 |  | System | Error Key 4 |  |  |  |  | long
INPUT_REGISTER | Read | 6984 |  | System | Error 1 Extra Info (MSB) |  |  |  |  | long
INPUT_REGISTER | Read | 6986 |  | System | Error 1 Extra Info (LSB) |  |  |  |  | long
INPUT_REGISTER | Read | 6988 |  | System | Error 2 Extra Info (MSB) |  |  |  |  | long
INPUT_REGISTER | Read | 6990 |  | System | Error 2 Extra Info (LSB) |  |  |  |  | long
INPUT_REGISTER | Read | 6992 |  | System | Error 3 Extra Info (MSB) |  |  |  |  | long
INPUT_REGISTER | Read | 6994 |  | System | Error 3 Extra Info (LSB) |  |  |  |  | long
INPUT_REGISTER | Read | 6996 |  | System | Error 4 Extra Info (MSB) |  |  |  |  | long
INPUT_REGISTER | Read | 6998 |  | System | Error 4 Extra Info (LSB) |  |  |  |  | long

## Slave14
Register Type | Permissions | Address | Bitblock Bit | Component | Name | Min | Max | Range | Unit | DataType | Float to Int Factor
HOLDING_REGISTER | Write | 7007 |  | DomesticHotWater Zm/Ems | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 7008 |  | DomesticHotWater Zm/Ems | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 7009 |  | DomesticHotWater Zm/Ems | Thermal Disinfection Setpoint | 65 | 75 |  | °C | int | x10
HOLDING_REGISTER | Write | 7010 |  | DomesticHotWater Zm | Setpoint Auto Day | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 7011 |  | DomesticHotWater Zm | Setpoint Auto Night | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 7012 |  | DomesticHotWater Zm | Setpoint Manual Day | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 7013 |  | DomesticHotWater Zm | Setpoint Manual Night | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 7014 |  | DomesticHotWater Zm | Setpoint Holiday | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 7015 |  | DomesticHotWater Zm/Ems | Circulation Pump Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 7016 |  | DomesticHotWater Zm/Ems | Circulation Pump Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 7017 |  | DomesticHotWater Zm/Ems | Disinfection Frequency | 0 | 7 | 0-Daily 1-Monday 2-Tuesday 3-Wednesday 4-Thursday 5-Friday 6-Saturday 7-Sunday |  | int
HOLDING_REGISTER | Write | 7018 |  | DomesticHotWater Zm/Ems | Disinfection Start Hour | 0 | 23 |  | h | int
HOLDING_REGISTER | Write | 7021 |  | DomesticHotWater Fm | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 7022 |  | DomesticHotWater Fm | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 7023 |  | DomesticHotWater Fm | Thermal Disinfection Setpoint | 65 | 75 |  | °C | int | x10
HOLDING_REGISTER | Write | 7024 |  | DomesticHotWater Fm | Setpoint Auto Day | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 7025 |  | DomesticHotWater Fm | Setpoint Auto Night | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 7026 |  | DomesticHotWater Fm | Setpoint Manual Day | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 7027 |  | DomesticHotWater Fm | Setpoint Manual Night | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 7028 |  | DomesticHotWater Fm | Setpoint Holiday | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 7029 |  | DomesticHotWater Fm | Circulation Pump Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 7030 |  | DomesticHotWater Fm | Circulation Pump Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 7031 |  | DomesticHotWater Fm | Disinfection Frequency | 0 | 7 | 0-Daily 1-Monday 2-Tuesday 3-Wednesday 4-Thursday 5-Friday 6-Saturday 7-Sunday |  | int
HOLDING_REGISTER | Write | 7032 |  | DomesticHotWater Fm | Disinfection Start Hour | 0 | 23 |  | h | int
HOLDING_REGISTER | Read | 7039 |  | Boiler | Control Type | 0 | 4 | 0-None 1-Safe 2-Ems 3-7Pole 4-Substation |  | int
HOLDING_REGISTER | Write | 7043 |  | AlternativeHeatSource | Operation Mode Request Auto Day | 20 | 99 |  | °C | int
HOLDING_REGISTER | Write | 7044 |  | AlternativeHeatSource | Operation Mode Request Auto Night | 20 | 99 |  | °C | int
HOLDING_REGISTER | Write | 7045 |  | AlternativeHeatSource | Operation Mode Request Manual Day | 20 | 99 |  | °C | int
HOLDING_REGISTER | Write | 7046 |  | AlternativeHeatSource | Operation Mode Request Manual Night | 20 | 99 |  | °C | int
HOLDING_REGISTER | Write | 7047 |  | AlternativeHeatSource | Operation Mode Request Holiday | 20 | 99 |  | °C | int
HOLDING_REGISTER | Write | 7048 |  | AlternativeHeatSource | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 7049 |  | AlternativeHeatSource | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 7050 |  | AlternativeHeatSource | Return Control Setpoint User | 10 | 70 |  | °C | int
HOLDING_REGISTER | Write | 7057 |  | HydraulicCircuit Zm | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 7058 |  | HydraulicCircuit Zm | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 7059 |  | HydraulicCircuit Zm | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7060 |  | HydraulicCircuit Zm | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7061 |  | HydraulicCircuit Zm | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7062 |  | HydraulicCircuit Zm | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7063 |  | HydraulicCircuit Zm | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7064 |  | HydraulicCircuit Zm | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 7070 |  | HydraulicCircuit 1 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 7071 |  | HydraulicCircuit 1 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 7072 |  | HydraulicCircuit 1 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7073 |  | HydraulicCircuit 1 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7074 |  | HydraulicCircuit 1 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7075 |  | HydraulicCircuit 1 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7076 |  | HydraulicCircuit 1 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7077 |  | HydraulicCircuit 1 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 7083 |  | HydraulicCircuit 2 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 7084 |  | HydraulicCircuit 2 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 7085 |  | HydraulicCircuit 2 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7086 |  | HydraulicCircuit 2 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7087 |  | HydraulicCircuit 2 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7088 |  | HydraulicCircuit 2 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7089 |  | HydraulicCircuit 2 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7090 |  | HydraulicCircuit 2 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 7096 |  | HydraulicCircuit 3 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 7097 |  | HydraulicCircuit 3 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 7098 |  | HydraulicCircuit 3 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7099 |  | HydraulicCircuit 3 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7100 |  | HydraulicCircuit 3 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7101 |  | HydraulicCircuit 3 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7102 |  | HydraulicCircuit 3 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7103 |  | HydraulicCircuit 3 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 7109 |  | HydraulicCircuit 4 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 7110 |  | HydraulicCircuit 4 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 7111 |  | HydraulicCircuit 4 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7112 |  | HydraulicCircuit 4 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7113 |  | HydraulicCircuit 4 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7114 |  | HydraulicCircuit 4 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7115 |  | HydraulicCircuit 4 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7116 |  | HydraulicCircuit 4 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 7122 |  | HydraulicCircuit 5 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 7123 |  | HydraulicCircuit 5 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 7124 |  | HydraulicCircuit 5 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7125 |  | HydraulicCircuit 5 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7126 |  | HydraulicCircuit 5 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7127 |  | HydraulicCircuit 5 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7128 |  | HydraulicCircuit 5 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7129 |  | HydraulicCircuit 5 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 7135 |  | HydraulicCircuit 6 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 7136 |  | HydraulicCircuit 6 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 7137 |  | HydraulicCircuit 6 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7138 |  | HydraulicCircuit 6 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7139 |  | HydraulicCircuit 6 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7140 |  | HydraulicCircuit 6 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7141 |  | HydraulicCircuit 6 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7142 |  | HydraulicCircuit 6 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 7148 |  | HydraulicCircuit 7 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 7149 |  | HydraulicCircuit 7 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 7150 |  | HydraulicCircuit 7 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7151 |  | HydraulicCircuit 7 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7152 |  | HydraulicCircuit 7 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7153 |  | HydraulicCircuit 7 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7154 |  | HydraulicCircuit 7 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7155 |  | HydraulicCircuit 7 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 7161 |  | HydraulicCircuit 8 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 7162 |  | HydraulicCircuit 8 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 7163 |  | HydraulicCircuit 8 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7164 |  | HydraulicCircuit 8 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7165 |  | HydraulicCircuit 8 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7166 |  | HydraulicCircuit 8 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7167 |  | HydraulicCircuit 8 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7168 |  | HydraulicCircuit 8 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 7201 |  | Heat Pump | Heat demand source | 0 | 2 | 0-Scheduler 1-System 2-Max_system_scheduler |  | int
HOLDING_REGISTER | Read | 7421 |  | Fresh Water Characteristics 3 | DHU Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 7422 |  | Fresh Water Characteristics 3 | Extra Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 7423 |  | Fresh Water Characteristics 3 | Maximum DHW Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 7424 |  | Fresh Water Characteristics 3 | On High Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 7425 |  | Fresh Water Characteristics 3 | On Low Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 7426 |  | Fresh Water Characteristics 3 | Fresh Water Type | 0 | 3 | 0-15/20l/min 1-27l/min 2-40l/min 3-60l/min |  | int
HOLDING_REGISTER | Read | 7427 |  | Fresh Water Characteristics 3 | Enable Alarm Output | 0 | 2 | 0-No 1-Yes 2-Inverted |  | int
HOLDING_REGISTER | Read | 7428 |  | Fresh Water Characteristics 3 | Buffer Cylinder Temperature Offset |  |  |  | K | int
HOLDING_REGISTER | Read | 7429 |  | Fresh Water Characteristics 3 | hrBitblock |  |  |  |  | int
| Read |  | 0 | Fresh Water | Buffer Cylinder Temperature Optimization Enabled |  |  |  |  | bit
| Read |  | 1 | Fresh Water | Impulse Enabled |  |  |  |  | bit
| Read |  | 2 | Fresh Water | Time Program Enabled |  |  |  |  | bit
HOLDING_REGISTER | Read | 7430 |  | Fresh Water Characteristics 3 | Minimum Buffer Cylinder Temperature Offset |  |  |  | K | int
HOLDING_REGISTER | Read | 7431 |  | Fresh Water Characteristics 2 | Circulation Pump Runs per Hour | 0 | 7 | 0-Undefined 1-1x3_minutes/h 2-2x3_minutes/h 3-3x3_minutes/h 4-4x3_minutes/h 5-5x3_minutes/h 6-6x3_minutes/h 7-Permanent |  | int
HOLDING_REGISTER | Read | 7432 |  | Fresh Water Characteristics 2 | Swich Hysteresis |  |  |  | K | int
HOLDING_REGISTER | Read | 7433 |  | Fresh Water Characteristics 2 | Thermal Disinfection Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 7434 |  | Fresh Water Characteristics 2 | Pre Heat Maximum Temperature |  |  |  | °C | int
INPUT_REGISTER | Read | 7000 |  | System | Own Outdoor temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7001 |  | System | Damped Own outdoor temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7004 |  | System | Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7008 |  | System | Active Functions 1 |  |  |  |  | int
INPUT_REGISTER | Read | 7009 |  | System | Active Functions 2 |  |  |  |  | int
INPUT_REGISTER | Read | 7015 |  | DomesticHotWater Zm | Charge Pump Running | 0 | 4 | 0-Stopping 1-Starting 2-Running 3-Off 4-Error |  | int
INPUT_REGISTER | Read | 7016 |  | DomesticHotWater Zm | Circulation Pump Running | 0 | 4 | 0-Stopping 1-Starting 2-Running 3-Off 4-Error |  | int
INPUT_REGISTER | Read | 7017 |  | DomesticHotWater Zm | Hydraulic State | 0 | 7 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Cold_load 6-Post_purge 7-Condense_protection |  | int
INPUT_REGISTER | Read | 7018 |  | DomesticHotWater Zm/Ems | Thermal Disinfection Status | 0 | 3 | 0-Off 1-On 2-Success 3-Error |  | int
INPUT_REGISTER | Read | 7019 |  | DomesticHotWater Zm/Ems | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 7020 |  | DomesticHotWater Zm/Ems | Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7021 |  | DomesticHotWater Zm/Ems | Current Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7031 |  | DomesticHotWater Fm | Charge Pump Running | 0 | 4 | 0-Stopping 1-Starting 2-Running 3-Off 4-Error |  | int
INPUT_REGISTER | Read | 7032 |  | DomesticHotWater Fm | Circulation Pump Running | 0 | 4 | 0-Stopping 1-Starting 2-Running 3-Off 4-Error |  | int
INPUT_REGISTER | Read | 7033 |  | DomesticHotWater Fm | Hydraulic State | 0 | 7 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Cold_load 6-Post_purge 7-Condense_protection |  | int
INPUT_REGISTER | Read | 7034 |  | DomesticHotWater Fm | Thermal Disinfection Status | 0 | 3 | 0-Off 1-On 2-Success 3-Error |  | int
INPUT_REGISTER | Read | 7035 |  | DomesticHotWater Fm | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 7036 |  | DomesticHotWater Fm | Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7037 |  | DomesticHotWater Fm | Current Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER |  | 7047 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 7048 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 7050 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 7052 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 7053 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 7054 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 7055 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 7056 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 7059 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 7060 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER | Read | 7063 |  | AlternativeHeatSource | Operating hours |  |  |  | h | long
INPUT_REGISTER | Read | 7065 |  | AlternativeHeatSource | Heat Source Starts |  |  |  |  | long
INPUT_REGISTER | Read | 7067 |  | AlternativeHeatSource | Heat Source Hours to Maintenance |  |  |  | h | int
INPUT_REGISTER | Read | 7069 |  | AlternativeHeatSource | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
| Read |  | 0 | AlternativeHeatSource | Is Heat Source On |  |  |  |  | bit
| Read |  | 1 | AlternativeHeatSource | Is Heat Source On Request |  |  |  |  | bit
INPUT_REGISTER | Read | 7087 |  | HydraulicCircuit Zm | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7088 |  | HydraulicCircuit Zm | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7089 |  | HydraulicCircuit Zm | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7090 |  | HydraulicCircuit Zm | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7091 |  | HydraulicCircuit Zm | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 7092 |  | HydraulicCircuit Zm | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 7093 |  | HydraulicCircuit Zm | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 7094 |  | HydraulicCircuit Zm | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 7095 |  | HydraulicCircuit Zm | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 7099 |  | HydraulicCircuit 1 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7100 |  | HydraulicCircuit 1 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7101 |  | HydraulicCircuit 1 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7102 |  | HydraulicCircuit 1 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7103 |  | HydraulicCircuit 1 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 7104 |  | HydraulicCircuit 1 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 7105 |  | HydraulicCircuit 1 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 7106 |  | HydraulicCircuit 1 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 7107 |  | HydraulicCircuit 1 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 7112 |  | HydraulicCircuit 2 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7113 |  | HydraulicCircuit 2 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7114 |  | HydraulicCircuit 2 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7115 |  | HydraulicCircuit 2 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7116 |  | HydraulicCircuit 2 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 7117 |  | HydraulicCircuit 2 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 7118 |  | HydraulicCircuit 2 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 7119 |  | HydraulicCircuit 2 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 7120 |  | HydraulicCircuit 2 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 7125 |  | HydraulicCircuit 3 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7126 |  | HydraulicCircuit 3 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7127 |  | HydraulicCircuit 3 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7128 |  | HydraulicCircuit 3 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7129 |  | HydraulicCircuit 3 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 7130 |  | HydraulicCircuit 3 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 7131 |  | HydraulicCircuit 3 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 7132 |  | HydraulicCircuit 3 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 7133 |  | HydraulicCircuit 3 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 7138 |  | HydraulicCircuit 4 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7139 |  | HydraulicCircuit 4 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7140 |  | HydraulicCircuit 4 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7141 |  | HydraulicCircuit 4 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7142 |  | HydraulicCircuit 4 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 7143 |  | HydraulicCircuit 4 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 7144 |  | HydraulicCircuit 4 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 7145 |  | HydraulicCircuit 4 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 7146 |  | HydraulicCircuit 4 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 7151 |  | HydraulicCircuit 5 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7152 |  | HydraulicCircuit 5 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7153 |  | HydraulicCircuit 5 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7154 |  | HydraulicCircuit 5 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7155 |  | HydraulicCircuit 5 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 7156 |  | HydraulicCircuit 5 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 7157 |  | HydraulicCircuit 5 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 7158 |  | HydraulicCircuit 5 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 7159 |  | HydraulicCircuit 5 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 7164 |  | HydraulicCircuit 6 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7165 |  | HydraulicCircuit 6 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7166 |  | HydraulicCircuit 6 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7167 |  | HydraulicCircuit 6 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7168 |  | HydraulicCircuit 6 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 7169 |  | HydraulicCircuit 6 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 7170 |  | HydraulicCircuit 6 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 7171 |  | HydraulicCircuit 6 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 7172 |  | HydraulicCircuit 6 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 7177 |  | HydraulicCircuit 7 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7178 |  | HydraulicCircuit 7 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7179 |  | HydraulicCircuit 7 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7180 |  | HydraulicCircuit 7 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7181 |  | HydraulicCircuit 7 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 7182 |  | HydraulicCircuit 7 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 7183 |  | HydraulicCircuit 7 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 7184 |  | HydraulicCircuit 7 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 7185 |  | HydraulicCircuit 7 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 7190 |  | HydraulicCircuit 8 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7191 |  | HydraulicCircuit 8 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7192 |  | HydraulicCircuit 8 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7193 |  | HydraulicCircuit 8 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7194 |  | HydraulicCircuit 8 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 7195 |  | HydraulicCircuit 8 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 7196 |  | HydraulicCircuit 8 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 7197 |  | HydraulicCircuit 8 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 7198 |  | HydraulicCircuit 8 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 7203 |  | i2c | Global Error State | 0 | 4 | 0-No_Error 1-i2c_driver_error 2-Wrong_Cycle_Time 3-Missing_Module_Slot 4-Module_Slot_Error |  | int
INPUT_REGISTER | Read | 7204 |  | i2c | Slot1 Module Detected |  |  | 0-Unknown 1-None 22-FM_CM 25-FM_SI 28-FM_MM 29-FM_MW 30-FM_AM 31-FM_CM2 |  | int
INPUT_REGISTER | Read | 7205 |  | i2c | Slot1 Error State |  |  | 0-No_Error 1-No_Response 2-Wrong_Module 3-Unsupported_Module 4-Internal_Sw_Error 5-Communication_Failed 6-Internal_Module_Error 7-Module_Not_Supported_Current_Variant 8-Module_Not_Suppported_In_Slot 9-Module_Count_Too_High 10-Module_Not_Supported_With_Connected_Boiler_Type |  | int
INPUT_REGISTER | Read | 7206 |  | i2c | Slot2 Module Detected |  |  | 0-Unknown 1-None 22-FM_CM 25-FM_SI 28-FM_MM 29-FM_MW 30-FM_AM 31-FM_CM2 |  | int
INPUT_REGISTER | Read | 7207 |  | i2c | Slot2 Error State |  |  | 0-No_Error 1-No_Response 2-Wrong_Module 3-Unsupported_Module 4-Internal_Sw_Error 5-Communication_Failed 6-Internal_Module_Error 7-Module_Not_Supported_Current_Variant 8-Module_Not_Suppported_In_Slot 9-Module_Count_Too_High 10-Module_Not_Supported_With_Connected_Boiler_Type |  | int
INPUT_REGISTER | Read | 7208 |  | i2c | Slot3 Module Detected |  |  | 0-Unknown 1-None 22-FM_CM 25-FM_SI 28-FM_MM 29-FM_MW 30-FM_AM 31-FM_CM2 |  | int
INPUT_REGISTER | Read | 7209 |  | i2c | Slot3 Error State |  |  | 0-No_Error 1-No_Response 2-Wrong_Module 3-Unsupported_Module 4-Internal_Sw_Error 5-Communication_Failed 6-Internal_Module_Error 7-Module_Not_Supported_Current_Variant 8-Module_Not_Suppported_In_Slot 9-Module_Count_Too_High 10-Module_Not_Supported_With_Connected_Boiler_Type |  | int
INPUT_REGISTER | Read | 7210 |  | i2c | Slot4 Module Detected |  |  | 0-Unknown 1-None 22-FM_CM 25-FM_SI 28-FM_MM 29-FM_MW 30-FM_AM 31-FM_CM2 |  | int
INPUT_REGISTER | Read | 7211 |  | i2c | Slot4 Error State |  |  | 0-No_Error 1-No_Response 2-Wrong_Module 3-Unsupported_Module 4-Internal_Sw_Error 5-Communication_Failed 6-Internal_Module_Error 7-Module_Not_Supported_Current_Variant 8-Module_Not_Suppported_In_Slot 9-Module_Count_Too_High 10-Module_Not_Supported_With_Connected_Boiler_Type |  | int
INPUT_REGISTER | Read | 7212 |  | i2c | Slot A Module Detected |  |  | 0-Unknown 1-None 26-ZM5313 27-ZM5311 |  | int
INPUT_REGISTER | Read | 7213 |  | i2c | Slot A Error State |  |  | 0-No_Error 1-No_Response 2-Wrong_Module 3-Unsupported_Module 4-Internal_Sw_Error 5-Communication_Failed 6-Internal_Module_Error 7-Module_Not_Supported_Current_Variant 8-Module_Not_Suppported_In_Slot 9-Module_Count_Too_High 10-Module_Not_Supported_With_Connected_Boiler_Type |  | int
INPUT_REGISTER | Read | 7214 |  | i2c | irBitblock |  |  |  |  | int
| Read |  | 0 | i2c | Component Error |  |  |  |  | bit
INPUT_REGISTER | Read | 7225 |  | fm-si | irBitblock |  |  |  |  | int
| Read |  | 0 | fm-si | Input 1 Error |  |  |  |  | bit
| Read |  | 1 | fm-si | Input 2 Error |  |  |  |  | bit
| Read |  | 2 | fm-si | Input 3 Error |  |  |  |  | bit
| Read |  | 3 | fm-si | Input 4 Error |  |  |  |  | bit
| Read |  | 4 | fm-si | Input 5 Error |  |  |  |  | bit
INPUT_REGISTER | Read | 7232 |  | Sdc | Demand Mode (Low Priority) | 0 | 2 | 0-Off 1-Take_Heat 2-Give_Heat |  | int
INPUT_REGISTER | Read | 7233 |  | Sdc | Demand Flow Temp (Low Priority) |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7234 |  | Sdc | Demand Mode (High Priority) | 0 | 2 | 0-Off 1-Take_Heat 2-Give_Heat |  | int
INPUT_REGISTER | Read | 7235 |  | Sdc | Demand Flow Temp (High Priority) |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7239 |  | Heat Pump | System return temperature for HP heating buffer |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7240 |  | Heat Pump | Buffer mid temperature for HP heating buffer |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7241 |  | Heat Pump | Buffer top temperature for HP heating buffer |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7242 |  | Heat Pump | Buffer bottom temperature for HP heating buffer |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7243 |  | Heat Pump | Return temperature FWR |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7244 |  | Heat Pump | Flow temperature FWV |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7245 |  | Heat Pump | Flow temperature HP |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7246 |  | Heat Pump | Return temperature HP |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7247 |  | Heat Pump | HMI State of HP Component | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 7248 |  | Heat Pump | HP current heat output |  |  |  | kW | signed int | x10
INPUT_REGISTER | Read | 7249 |  | Heat Pump | HP current electrical power consumption | 0 | 10000 |  | kW | int | x10
INPUT_REGISTER | Read | 7250 |  | Heat Pump | HP Smart grid mode | 0 | 3 | 0-normal_charging_grid 1-low_charging_grid 2-high_charging_grid 3-free_charging_grid |  | int
INPUT_REGISTER | Read | 7251 |  | Heat Pump | Heat demand temperature set point |  |  |  | °C | int
INPUT_REGISTER | Read | 7252 |  | Heat Pump | heatPumpStatusIrBitblock | 0 |  |  |  | int
INPUT_REGISTER | Read | 7253 |  | Heat Pump | Ambient Temperature HP |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7254 |  | Heat Pump | HP silent mode | 0 | 3 | 0-standard_mode 1-silent_mode 2-super_silent_mode 3-night_mode |  | int
INPUT_REGISTER | Read | 7255 |  | Heat Pump | Heat Pump Heat Request Temperature |  |  |  | °C | int
INPUT_REGISTER | Read | 7256 |  | Heat Pump | heatPumpIrBitblock |  |  |  |  | int
INPUT_REGISTER | Read | 7265 |  | System | Open Notifications Count |  |  |  |  | int
INPUT_REGISTER | Read | 7266 |  | System | Error Key 5 |  |  |  |  | long
INPUT_REGISTER | Read | 7268 |  | System | Error Key 6 |  |  |  |  | long
INPUT_REGISTER | Read | 7270 |  | System | Error Key 7 |  |  |  |  | long
INPUT_REGISTER | Read | 7272 |  | System | Error Key 8 |  |  |  |  | long
INPUT_REGISTER | Read | 7274 |  | System | Error Key 9 |  |  |  |  | long
INPUT_REGISTER | Read | 7276 |  | System | Error Key 10 |  |  |  |  | long
INPUT_REGISTER | Read | 7278 |  | Chp / EC Power | Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7279 |  | Chp / EC Power | Return Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7280 |  | Chp | Flue Gas Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7281 |  | Chp | Motor Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7282 |  | Chp / EC Power | Current Generator Power |  |  |  | kW | int
INPUT_REGISTER | Read | 7283 |  | Chp | Current Power Setpoint |  |  |  | kW | int
INPUT_REGISTER | Read | 7284 |  | Chp / EC Power | Operation Hours |  |  |  | h | long
INPUT_REGISTER | Read | 7286 |  | Chp / EC Power | Number of starts |  |  |  |  | long
INPUT_REGISTER | Read | 7288 |  | Chp / EC Power | Hours to Maintenance |  |  |  | h | int
INPUT_REGISTER | Read | 7290 |  | Chp | Output Power Setpoint |  |  |  | kW | int
INPUT_REGISTER | Read | 7291 |  | Chp | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 7296 |  | Chp | irBitblock |  |  |  |  | int
| Read |  | 0 | Chp | Warning |  |  |  |  | bit
| Read |  | 1 | Chp / EC Power | Malfunction |  |  |  |  | bit
| Read |  | 2 | Chp / EC Power | Controlled Shutdown |  |  |  |  | bit
| Read |  | 3 | Chp / EC Power | Generator On |  |  |  |  | bit
| Read |  | 4 | Chp | Automatic On |  |  |  |  | bit
| Read |  | 5 | Chp / EC Power | Automatic Ready |  |  |  |  | bit
| Read |  | 11 | Chp / EC Power | Output On Request |  |  |  |  | bit
INPUT_REGISTER | Read | 7304 |  | Water Treatment Module | Program Step |  |  | 20-140: Desalination not active 10000-10810: One time desalination 20000-20810: Automatic desalination 30000-30260: Stationary operation |  | int
INPUT_REGISTER | Read | 7305 |  | Water Treatment Module | Temperature Desalinization |  |  |  | °C | int | x10
INPUT_REGISTER | Read | 7306 |  | Water Treatment Module | Volume Flow |  |  |  | L/min | int | x10
INPUT_REGISTER | Read | 7307 |  | Water Treatment Module | Conductivity system |  |  |  | uS/cm | int | x10
INPUT_REGISTER | Read | 7308 |  | Water Treatment Module | Conductivity cartridge |  |  |  | uS/cm | int | x10
INPUT_REGISTER | Read | 7309 |  | Water Treatment Module | Cartridge Capacity |  |  |  | % | int
INPUT_REGISTER | Read | 7313 |  | Solar Data | Collector temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7314 |  | Solar Data | Temperature cylinder bottom |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7315 |  | Solar Data | Solar pump modulation setpoint |  |  |  | % | int
INPUT_REGISTER | Read | 7316 |  | Solar | Solar pump status | 0 | 19 | 1-TestMod 2-BlckProt 3-No heat 4-Ht avail 5-SolOff 6-MaxCyl 7-MaxColl 8-MinColl 9-FrostP 10-VacFct 11-SwChck 12-MixPrio 13-Switch 14-Priority 15-ThermD 16-MixCal 17-MixOpn 18-MixCl 19-MixOff |  | int
INPUT_REGISTER | Read | 7317 |  | Solar Data | Heat exchanger temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7318 |  | Solar Data | Heat exchanger pump modulation setpoint |  |  |  | % | int
INPUT_REGISTER | Read | 7319 |  | Solar | Heat exchanger pump status | 0 | 19 | 1-TestMod 2-BlckProt 3-No heat 4-Ht avail 5-SolOff 6-MaxCyl 7-MaxColl 8-MinColl 9-FrostP 10-VacFct 11-SwChck 12-MixPrio 13-Switch 14-Priority 15-ThermD 16-MixCal 17-MixOpn 18-MixCl 19-MixOff |  | int
INPUT_REGISTER | Read | 7320 |  | Solar Data | Temperature cylinder 3 top |  |  |  | °C | int | x10
INPUT_REGISTER | Read | 7321 |  | Solar Data | Reload pump modulation setpoint |  |  |  | % | int
INPUT_REGISTER | Read | 7322 |  | Solar | Reload pump status | 0 | 19 | 1-TestMod 2-BlckProt 3-No heat 4-Ht avail 5-SolOff 6-MaxCyl 7-MaxColl 8-MinColl 9-FrostP 10-VacFct 11-SwChck 12-MixPrio 13-Switch 14-Priority 15-ThermD 16-MixCal 17-MixOpn 18-MixCl 19-MixOff |  | int
INPUT_REGISTER | Read | 7323 |  | Solar | Pump therm. disinfect. status | 0 | 19 | 1-TestMod 2-BlckProt 3-No heat 4-Ht avail 5-SolOff 6-MaxCyl 7-MaxColl 8-MinColl 9-FrostP 10-VacFct 11-SwChck 12-MixPrio 13-Switch 14-Priority 15-ThermD 16-MixCal 17-MixOpn 18-MixCl 19-MixOff |  | int
INPUT_REGISTER | Read | 7324 |  | Solar Yield | Flow temperature heat meter |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7325 |  | Solar Yield | Return temperature heat meter |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7326 |  | Solar Yield | Heat count pulse counter | 0 | 15 |  |  | int
INPUT_REGISTER | Read | 7327 |  | Solar Yield | Solar yield per month |  |  |  | kWh | long | x10
INPUT_REGISTER | Read | 7329 |  | Solar Yield | Solar yield per year |  |  |  | kWh | long | x10
INPUT_REGISTER | Read | 7331 |  | Solar Yield | Last hour solar yield |  |  |  | kWh | long | x10
INPUT_REGISTER | Read | 7333 |  | Solar Yield | Solar yield per day |  |  |  | kWh | long | x10
INPUT_REGISTER | Read | 7335 |  | Solar Yield | Solar yield since installation |  |  |  | kWh | long | x10
INPUT_REGISTER | Read | 7337 |  | Solar | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 7338 |  | Solar Data | Hydraulic configuration |  |  |  |  | int
| Read |  | 0 | Solar | Option 1 active |  |  |  |  | bit
| Read |  | 1 | Solar | Option A active |  |  |  |  | bit
| Read |  | 2 | Solar | Option B active |  |  |  |  | bit
| Read |  | 3 | Solar | Option C active |  |  |  |  | bit
| Read |  | 4 | Solar | Option D active |  |  |  |  | bit
| Read |  | 5 | Solar | Option E active |  |  |  |  | bit
| Read |  | 6 | Solar | Option F active |  |  |  |  | bit
| Read |  | 7 | Solar | Option G active |  |  |  |  | bit
| Read |  | 8 | Solar | Option H active |  |  |  |  | bit
| Read |  | 9 | Solar | Option I active |  |  |  |  | bit
| Read |  | 10 | Solar | Option J active |  |  |  |  | bit
| Read |  | 11 | Solar | Option K active |  |  |  |  | bit
| Read |  | 12 | Solar | Option L active |  |  |  |  | bit
| Read |  | 13 | Solar | Option M active |  |  |  |  | bit
| Read |  | 14 | Solar | Option N active |  |  |  |  | bit
| Read |  | 15 | Solar | Option P active |  |  |  |  | bit
INPUT_REGISTER | Read | 7339 |  | Solar Data | irBitblock |  |  |  |  | int
| Read |  | 0 | Solar | Is Active |  |  |  |  | bit
INPUT_REGISTER |  | 7400 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 7401 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 7402 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 7403 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 7404 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 7405 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 7406 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 7407 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 7408 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 7409 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 7410 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 7411 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 7412 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 7413 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER | Read | 7422 |  | Energy Monitoring | Heat Output |  |  |  | kW | signed int | x10
INPUT_REGISTER | Read | 7423 |  | Energy Monitoring | Gas Consumption (LCV) |  |  |  | kW | signed int | x10
INPUT_REGISTER | Read | 7425 |  | Energy Monitoring | Electrical Power |  |  |  | W | int
INPUT_REGISTER | Read | 7430 |  | Fresh Water Characteristics 1 | DHW Out Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7431 |  | Fresh Water Characteristics 1 | DHW Volume Flow |  |  |  | L/min | signed int | x10
INPUT_REGISTER | Read | 7432 |  | Fresh Water Characteristics 1 | Prim In Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7433 |  | Fresh Water Characteristics 1 | DHW In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7434 |  | Fresh Water Characteristics 1 | Primary Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 7435 |  | Fresh Water Characteristics 1 | Request DHW Out Temperature |  |  |  | °C | int
INPUT_REGISTER | Read | 7436 |  | Fresh Water Characteristics 1 | Status Request DHW Out Temperature | 0 | 9 | 0-Off 1-DHWRed 2-DHW 3-Sol_red 4-Once_on 5-Therm_d 6-DlyHtUp 7-Preheat_start 8-Preheat_normal 9-No_eq |  | int
INPUT_REGISTER | Read | 7437 |  | Fresh Water Characteristics 2 | Circulation Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 7438 |  | Fresh Water Characteristics 2 | Status Circulation Pump | 0 | 8 | 0-Undefined 1-Test 2-BlckProt 3-No_req 4-AutoOff 5-AutoOn 6-Therm_d 7-Sys_Off 8-DlyHtUp |  | int
INPUT_REGISTER | Read | 7439 |  | Fresh Water Characteristics 2 | Return Valve Modulation Request |  |  |  | % | int
INPUT_REGISTER | Read | 7440 |  | Fresh Water Characteristics 2 | Valve State | 0 | 5 | 0-Undefined 1-TestMod 2-BlckProt 3-Mix_cl 4-Mix_opn 5-Sys_Off |  | int
INPUT_REGISTER | Read | 7441 |  | Fresh Water Characteristics 2 | Return Valve Buffer Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7442 |  | Fresh Water Characteristics 2 | Disinfection Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 7443 |  | Fresh Water Characteristics 2 | Pump State | 0 | 5 | 0-Undefined 1-TestMod 2-BlckPro 3-No_eq 4-Ht_req 5-Sys_Off |  | int
INPUT_REGISTER | Read | 7444 |  | Fresh Water Characteristics 1 | DHW Valve Power |  |  |  | % | int
INPUT_REGISTER | Read | 7445 |  | Fresh Water Characteristics 2 | Total Flow |  |  |  | L/min | int | x10
INPUT_REGISTER | Read | 7446 |  | Fresh Water 2 | Module 2 DHW Out Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7447 |  | Fresh Water 2 | Module 2 DHW Volume Flow |  |  |  | L/min | signed int | x10
INPUT_REGISTER | Read | 7448 |  | Fresh Water 2 | Module 2 Prim In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7449 |  | Fresh Water 2 | Module 2 DHW In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7450 |  | Fresh Water 2 | Module 2 DHW Valve Power |  |  |  | % | int
INPUT_REGISTER | Read | 7451 |  | Fresh Water 2 | Module 2 Prim Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 7452 |  | Fresh Water 2 | Module 2 Status Prim Pump |  |  |  |  | int
INPUT_REGISTER | Read | 7453 |  | Fresh Water 3 | Module 3 DHW Out Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7454 |  | Fresh Water 3 | Module 3 DHW Volume Flow |  |  |  | L/min | signed int | x10
INPUT_REGISTER | Read | 7455 |  | Fresh Water 3 | Module 3 Prim In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7456 |  | Fresh Water 3 | Module 3 DHW In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7457 |  | Fresh Water 3 | Module 3 DHW Valve Power |  |  |  | % | int
INPUT_REGISTER | Read | 7458 |  | Fresh Water 3 | Module 3 Prim Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 7459 |  | Fresh Water 3 | Module 3 Status Prim Pump |  |  |  |  | int
INPUT_REGISTER | Read | 7460 |  | Fresh Water 4 | Module 4 DHW Out Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7461 |  | Fresh Water 4 | Module 4 DHW Volume Flow |  |  |  | L/min | signed int | x10
INPUT_REGISTER | Read | 7462 |  | Fresh Water 4 | Module 4 Prim In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7463 |  | Fresh Water 4 | Module 4 DHW In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7464 |  | Fresh Water 4 | Module 4 DHW ValvePower |  |  |  | % | int
INPUT_REGISTER | Read | 7465 |  | Fresh Water 4 | Module 4 Prim Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 7466 |  | Fresh Water 4 | Module 4 Status Primary Pump |  |  |  |  | int
INPUT_REGISTER | Read | 7467 |  | Fresh Water | Fresh Water Hmi State |  |  |  |  | int
INPUT_REGISTER | Read | 7468 |  | Fresh Water Characteristics 3 | Fresh Water Configurations |  |  |  |  | int
| Read |  | 0 | Fresh Water | Option 2 active |  |  |  |  | bit
| Read |  | 1 | Fresh Water | Option A active |  |  |  |  | bit
| Read |  | 2 | Fresh Water | Option B active |  |  |  |  | bit
| Read |  | 3 | Fresh Water | Option C active |  |  |  |  | bit
| Read |  | 4 | Fresh Water | Option D active |  |  |  |  | bit
| Read |  | 5 | Fresh Water | Option E active |  |  |  |  | bit
| Read |  | 6 | Fresh Water | Option E active cascade module 2 active |  |  |  |  | bit
| Read |  | 7 | Fresh Water | Option E active cascade module 3 active |  |  |  |  | bit
| Read |  | 8 | Fresh Water | Option E active cascade module 4 active |  |  |  |  | bit
| Read |  | 9 | Fresh Water | Is Active |  |  |  |  | bit
INPUT_REGISTER | Read | 7476 |  | System | Error Key 1 |  |  |  |  | long
INPUT_REGISTER | Read | 7478 |  | System | Error Key 2 |  |  |  |  | long
INPUT_REGISTER | Read | 7480 |  | System | Error Key 3 |  |  |  |  | long
INPUT_REGISTER | Read | 7482 |  | System | Error Key 4 |  |  |  |  | long
INPUT_REGISTER | Read | 7484 |  | System | Error 1 Extra Info (MSB) |  |  |  |  | long
INPUT_REGISTER | Read | 7486 |  | System | Error 1 Extra Info (LSB) |  |  |  |  | long
INPUT_REGISTER | Read | 7488 |  | System | Error 2 Extra Info (MSB) |  |  |  |  | long
INPUT_REGISTER | Read | 7490 |  | System | Error 2 Extra Info (LSB) |  |  |  |  | long
INPUT_REGISTER | Read | 7492 |  | System | Error 3 Extra Info (MSB) |  |  |  |  | long
INPUT_REGISTER | Read | 7494 |  | System | Error 3 Extra Info (LSB) |  |  |  |  | long
INPUT_REGISTER | Read | 7496 |  | System | Error 4 Extra Info (MSB) |  |  |  |  | long
INPUT_REGISTER | Read | 7498 |  | System | Error 4 Extra Info (LSB) |  |  |  |  | long

## Slave15
Register Type | Permissions | Address | Bitblock Bit | Component | Name | Min | Max | Range | Unit | DataType | Float to Int Factor
HOLDING_REGISTER | Write | 7507 |  | DomesticHotWater Zm/Ems | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 7508 |  | DomesticHotWater Zm/Ems | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 7509 |  | DomesticHotWater Zm/Ems | Thermal Disinfection Setpoint | 65 | 75 |  | °C | int | x10
HOLDING_REGISTER | Write | 7510 |  | DomesticHotWater Zm | Setpoint Auto Day | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 7511 |  | DomesticHotWater Zm | Setpoint Auto Night | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 7512 |  | DomesticHotWater Zm | Setpoint Manual Day | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 7513 |  | DomesticHotWater Zm | Setpoint Manual Night | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 7514 |  | DomesticHotWater Zm | Setpoint Holiday | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 7515 |  | DomesticHotWater Zm/Ems | Circulation Pump Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 7516 |  | DomesticHotWater Zm/Ems | Circulation Pump Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 7517 |  | DomesticHotWater Zm/Ems | Disinfection Frequency | 0 | 7 | 0-Daily 1-Monday 2-Tuesday 3-Wednesday 4-Thursday 5-Friday 6-Saturday 7-Sunday |  | int
HOLDING_REGISTER | Write | 7518 |  | DomesticHotWater Zm/Ems | Disinfection Start Hour | 0 | 23 |  | h | int
HOLDING_REGISTER | Write | 7521 |  | DomesticHotWater Fm | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 7522 |  | DomesticHotWater Fm | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 7523 |  | DomesticHotWater Fm | Thermal Disinfection Setpoint | 65 | 75 |  | °C | int | x10
HOLDING_REGISTER | Write | 7524 |  | DomesticHotWater Fm | Setpoint Auto Day | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 7525 |  | DomesticHotWater Fm | Setpoint Auto Night | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 7526 |  | DomesticHotWater Fm | Setpoint Manual Day | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 7527 |  | DomesticHotWater Fm | Setpoint Manual Night | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 7528 |  | DomesticHotWater Fm | Setpoint Holiday | 20 | 90 |  | °C | int | x10
HOLDING_REGISTER | Write | 7529 |  | DomesticHotWater Fm | Circulation Pump Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 7530 |  | DomesticHotWater Fm | Circulation Pump Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 7531 |  | DomesticHotWater Fm | Disinfection Frequency | 0 | 7 | 0-Daily 1-Monday 2-Tuesday 3-Wednesday 4-Thursday 5-Friday 6-Saturday 7-Sunday |  | int
HOLDING_REGISTER | Write | 7532 |  | DomesticHotWater Fm | Disinfection Start Hour | 0 | 23 |  | h | int
HOLDING_REGISTER | Read | 7539 |  | Boiler | Control Type | 0 | 4 | 0-None 1-Safe 2-Ems 3-7Pole 4-Substation |  | int
HOLDING_REGISTER | Write | 7543 |  | AlternativeHeatSource | Operation Mode Request Auto Day | 20 | 99 |  | °C | int
HOLDING_REGISTER | Write | 7544 |  | AlternativeHeatSource | Operation Mode Request Auto Night | 20 | 99 |  | °C | int
HOLDING_REGISTER | Write | 7545 |  | AlternativeHeatSource | Operation Mode Request Manual Day | 20 | 99 |  | °C | int
HOLDING_REGISTER | Write | 7546 |  | AlternativeHeatSource | Operation Mode Request Manual Night | 20 | 99 |  | °C | int
HOLDING_REGISTER | Write | 7547 |  | AlternativeHeatSource | Operation Mode Request Holiday | 20 | 99 |  | °C | int
HOLDING_REGISTER | Write | 7548 |  | AlternativeHeatSource | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 7549 |  | AlternativeHeatSource | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 7550 |  | AlternativeHeatSource | Return Control Setpoint User | 10 | 70 |  | °C | int
HOLDING_REGISTER | Write | 7557 |  | HydraulicCircuit Zm | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 7558 |  | HydraulicCircuit Zm | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 7559 |  | HydraulicCircuit Zm | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7560 |  | HydraulicCircuit Zm | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7561 |  | HydraulicCircuit Zm | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7562 |  | HydraulicCircuit Zm | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7563 |  | HydraulicCircuit Zm | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7564 |  | HydraulicCircuit Zm | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 7570 |  | HydraulicCircuit 1 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 7571 |  | HydraulicCircuit 1 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 7572 |  | HydraulicCircuit 1 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7573 |  | HydraulicCircuit 1 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7574 |  | HydraulicCircuit 1 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7575 |  | HydraulicCircuit 1 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7576 |  | HydraulicCircuit 1 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7577 |  | HydraulicCircuit 1 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 7583 |  | HydraulicCircuit 2 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 7584 |  | HydraulicCircuit 2 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 7585 |  | HydraulicCircuit 2 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7586 |  | HydraulicCircuit 2 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7587 |  | HydraulicCircuit 2 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7588 |  | HydraulicCircuit 2 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7589 |  | HydraulicCircuit 2 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7590 |  | HydraulicCircuit 2 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 7596 |  | HydraulicCircuit 3 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 7597 |  | HydraulicCircuit 3 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 7598 |  | HydraulicCircuit 3 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7599 |  | HydraulicCircuit 3 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7600 |  | HydraulicCircuit 3 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7601 |  | HydraulicCircuit 3 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7602 |  | HydraulicCircuit 3 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7603 |  | HydraulicCircuit 3 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 7609 |  | HydraulicCircuit 4 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 7610 |  | HydraulicCircuit 4 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 7611 |  | HydraulicCircuit 4 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7612 |  | HydraulicCircuit 4 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7613 |  | HydraulicCircuit 4 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7614 |  | HydraulicCircuit 4 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7615 |  | HydraulicCircuit 4 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7616 |  | HydraulicCircuit 4 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 7622 |  | HydraulicCircuit 5 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 7623 |  | HydraulicCircuit 5 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 7624 |  | HydraulicCircuit 5 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7625 |  | HydraulicCircuit 5 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7626 |  | HydraulicCircuit 5 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7627 |  | HydraulicCircuit 5 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7628 |  | HydraulicCircuit 5 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7629 |  | HydraulicCircuit 5 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 7635 |  | HydraulicCircuit 6 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 7636 |  | HydraulicCircuit 6 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 7637 |  | HydraulicCircuit 6 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7638 |  | HydraulicCircuit 6 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7639 |  | HydraulicCircuit 6 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7640 |  | HydraulicCircuit 6 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7641 |  | HydraulicCircuit 6 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7642 |  | HydraulicCircuit 6 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 7648 |  | HydraulicCircuit 7 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 7649 |  | HydraulicCircuit 7 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 7650 |  | HydraulicCircuit 7 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7651 |  | HydraulicCircuit 7 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7652 |  | HydraulicCircuit 7 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7653 |  | HydraulicCircuit 7 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7654 |  | HydraulicCircuit 7 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7655 |  | HydraulicCircuit 7 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 7661 |  | HydraulicCircuit 8 | Operation Mode (Auto/Manual) | 0 | 1 | 0-Automatic 1-Manual |  | int
HOLDING_REGISTER | Write | 7662 |  | HydraulicCircuit 8 | Manual Operation Mode (Night/Day) | 0 | 1 | 0-Manual_Night 1-Manual_Day |  | int
HOLDING_REGISTER | Write | 7663 |  | HydraulicCircuit 8 | Auto Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7664 |  | HydraulicCircuit 8 | Auto Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7665 |  | HydraulicCircuit 8 | Manual Day Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7666 |  | HydraulicCircuit 8 | Manual Night Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7667 |  | HydraulicCircuit 8 | Holiday Room Setpoint | 5 | 35 |  | °C | int | x10
HOLDING_REGISTER | Write | 7668 |  | HydraulicCircuit 8 | Offset | -15 | 15 |  | K | signed int | x10
HOLDING_REGISTER | Write | 7701 |  | Heat Pump | Heat demand source | 0 | 2 | 0-Scheduler 1-System 2-Max_system_scheduler |  | int
HOLDING_REGISTER | Read | 7921 |  | Fresh Water Characteristics 3 | DHU Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 7922 |  | Fresh Water Characteristics 3 | Extra Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 7923 |  | Fresh Water Characteristics 3 | Maximum DHW Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 7924 |  | Fresh Water Characteristics 3 | On High Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 7925 |  | Fresh Water Characteristics 3 | On Low Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 7926 |  | Fresh Water Characteristics 3 | Fresh Water Type | 0 | 3 | 0-15/20l/min 1-27l/min 2-40l/min 3-60l/min |  | int
HOLDING_REGISTER | Read | 7927 |  | Fresh Water Characteristics 3 | Enable Alarm Output | 0 | 2 | 0-No 1-Yes 2-Inverted |  | int
HOLDING_REGISTER | Read | 7928 |  | Fresh Water Characteristics 3 | Buffer Cylinder Temperature Offset |  |  |  | K | int
HOLDING_REGISTER | Read | 7929 |  | Fresh Water Characteristics 3 | hrBitblock |  |  |  |  | int
| Read |  | 0 | Fresh Water | Buffer Cylinder Temperature Optimization Enabled |  |  |  |  | bit
| Read |  | 1 | Fresh Water | Impulse Enabled |  |  |  |  | bit
| Read |  | 2 | Fresh Water | Time Program Enabled |  |  |  |  | bit
HOLDING_REGISTER | Read | 7930 |  | Fresh Water Characteristics 3 | Minimum Buffer Cylinder Temperature Offset |  |  |  | K | int
HOLDING_REGISTER | Read | 7931 |  | Fresh Water Characteristics 2 | Circulation Pump Runs per Hour | 0 | 7 | 0-Undefined 1-1x3_minutes/h 2-2x3_minutes/h 3-3x3_minutes/h 4-4x3_minutes/h 5-5x3_minutes/h 6-6x3_minutes/h 7-Permanent |  | int
HOLDING_REGISTER | Read | 7932 |  | Fresh Water Characteristics 2 | Swich Hysteresis |  |  |  | K | int
HOLDING_REGISTER | Read | 7933 |  | Fresh Water Characteristics 2 | Thermal Disinfection Temperature Setpoint |  |  |  | °C | int
HOLDING_REGISTER | Read | 7934 |  | Fresh Water Characteristics 2 | Pre Heat Maximum Temperature |  |  |  | °C | int
INPUT_REGISTER | Read | 7500 |  | System | Own Outdoor temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7501 |  | System | Damped Own outdoor temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7504 |  | System | Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7508 |  | System | Active Functions 1 |  |  |  |  | int
INPUT_REGISTER | Read | 7509 |  | System | Active Functions 2 |  |  |  |  | int
INPUT_REGISTER | Read | 7515 |  | DomesticHotWater Zm | Charge Pump Running | 0 | 4 | 0-Stopping 1-Starting 2-Running 3-Off 4-Error |  | int
INPUT_REGISTER | Read | 7516 |  | DomesticHotWater Zm | Circulation Pump Running | 0 | 4 | 0-Stopping 1-Starting 2-Running 3-Off 4-Error |  | int
INPUT_REGISTER | Read | 7517 |  | DomesticHotWater Zm | Hydraulic State | 0 | 7 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Cold_load 6-Post_purge 7-Condense_protection |  | int
INPUT_REGISTER | Read | 7518 |  | DomesticHotWater Zm/Ems | Thermal Disinfection Status | 0 | 3 | 0-Off 1-On 2-Success 3-Error |  | int
INPUT_REGISTER | Read | 7519 |  | DomesticHotWater Zm/Ems | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 7520 |  | DomesticHotWater Zm/Ems | Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7521 |  | DomesticHotWater Zm/Ems | Current Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7531 |  | DomesticHotWater Fm | Charge Pump Running | 0 | 4 | 0-Stopping 1-Starting 2-Running 3-Off 4-Error |  | int
INPUT_REGISTER | Read | 7532 |  | DomesticHotWater Fm | Circulation Pump Running | 0 | 4 | 0-Stopping 1-Starting 2-Running 3-Off 4-Error |  | int
INPUT_REGISTER | Read | 7533 |  | DomesticHotWater Fm | Hydraulic State | 0 | 7 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Cold_load 6-Post_purge 7-Condense_protection |  | int
INPUT_REGISTER | Read | 7534 |  | DomesticHotWater Fm | Thermal Disinfection Status | 0 | 3 | 0-Off 1-On 2-Success 3-Error |  | int
INPUT_REGISTER | Read | 7535 |  | DomesticHotWater Fm | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 7536 |  | DomesticHotWater Fm | Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7537 |  | DomesticHotWater Fm | Current Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER |  | 7547 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 7548 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 7550 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 7552 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 7553 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 7554 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 7555 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 7556 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 7559 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 7560 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER | Read | 7563 |  | AlternativeHeatSource | Operating hours |  |  |  | h | long
INPUT_REGISTER | Read | 7565 |  | AlternativeHeatSource | Heat Source Starts |  |  |  |  | long
INPUT_REGISTER | Read | 7567 |  | AlternativeHeatSource | Heat Source Hours to Maintenance |  |  |  | h | int
INPUT_REGISTER | Read | 7569 |  | AlternativeHeatSource | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
| Read |  | 0 | AlternativeHeatSource | Is Heat Source On |  |  |  |  | bit
| Read |  | 1 | AlternativeHeatSource | Is Heat Source On Request |  |  |  |  | bit
INPUT_REGISTER | Read | 7587 |  | HydraulicCircuit Zm | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7588 |  | HydraulicCircuit Zm | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7589 |  | HydraulicCircuit Zm | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7590 |  | HydraulicCircuit Zm | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7591 |  | HydraulicCircuit Zm | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 7592 |  | HydraulicCircuit Zm | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 7593 |  | HydraulicCircuit Zm | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 7594 |  | HydraulicCircuit Zm | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 7595 |  | HydraulicCircuit Zm | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 7599 |  | HydraulicCircuit 1 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7600 |  | HydraulicCircuit 1 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7601 |  | HydraulicCircuit 1 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7602 |  | HydraulicCircuit 1 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7603 |  | HydraulicCircuit 1 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 7604 |  | HydraulicCircuit 1 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 7605 |  | HydraulicCircuit 1 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 7606 |  | HydraulicCircuit 1 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 7607 |  | HydraulicCircuit 1 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 7612 |  | HydraulicCircuit 2 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7613 |  | HydraulicCircuit 2 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7614 |  | HydraulicCircuit 2 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7615 |  | HydraulicCircuit 2 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7616 |  | HydraulicCircuit 2 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 7617 |  | HydraulicCircuit 2 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 7618 |  | HydraulicCircuit 2 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 7619 |  | HydraulicCircuit 2 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 7620 |  | HydraulicCircuit 2 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 7625 |  | HydraulicCircuit 3 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7626 |  | HydraulicCircuit 3 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7627 |  | HydraulicCircuit 3 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7628 |  | HydraulicCircuit 3 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7629 |  | HydraulicCircuit 3 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 7630 |  | HydraulicCircuit 3 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 7631 |  | HydraulicCircuit 3 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 7632 |  | HydraulicCircuit 3 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 7633 |  | HydraulicCircuit 3 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 7638 |  | HydraulicCircuit 4 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7639 |  | HydraulicCircuit 4 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7640 |  | HydraulicCircuit 4 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7641 |  | HydraulicCircuit 4 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7642 |  | HydraulicCircuit 4 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 7643 |  | HydraulicCircuit 4 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 7644 |  | HydraulicCircuit 4 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 7645 |  | HydraulicCircuit 4 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 7646 |  | HydraulicCircuit 4 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 7651 |  | HydraulicCircuit 5 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7652 |  | HydraulicCircuit 5 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7653 |  | HydraulicCircuit 5 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7654 |  | HydraulicCircuit 5 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7655 |  | HydraulicCircuit 5 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 7656 |  | HydraulicCircuit 5 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 7657 |  | HydraulicCircuit 5 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 7658 |  | HydraulicCircuit 5 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 7659 |  | HydraulicCircuit 5 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 7664 |  | HydraulicCircuit 6 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7665 |  | HydraulicCircuit 6 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7666 |  | HydraulicCircuit 6 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7667 |  | HydraulicCircuit 6 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7668 |  | HydraulicCircuit 6 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 7669 |  | HydraulicCircuit 6 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 7670 |  | HydraulicCircuit 6 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 7671 |  | HydraulicCircuit 6 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 7672 |  | HydraulicCircuit 6 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 7677 |  | HydraulicCircuit 7 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7678 |  | HydraulicCircuit 7 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7679 |  | HydraulicCircuit 7 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7680 |  | HydraulicCircuit 7 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7681 |  | HydraulicCircuit 7 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 7682 |  | HydraulicCircuit 7 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 7683 |  | HydraulicCircuit 7 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 7684 |  | HydraulicCircuit 7 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 7685 |  | HydraulicCircuit 7 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 7690 |  | HydraulicCircuit 8 | Room Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7691 |  | HydraulicCircuit 8 | Current Room Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7692 |  | HydraulicCircuit 8 | Flow Temperature Setpoint |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7693 |  | HydraulicCircuit 8 | Current Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7694 |  | HydraulicCircuit 8 | Mixer Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 7695 |  | HydraulicCircuit 8 | Pump Modulation |  |  |  | % | int
INPUT_REGISTER | Read | 7696 |  | HydraulicCircuit 8 | Current Operation Mode | 0 | 4 | 0-Manual_Night 1-Manual_Day 2-Holiday 3-Auto_Night 4-Auto_Day |  | int
INPUT_REGISTER | Read | 7697 |  | HydraulicCircuit 8 | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 7698 |  | HydraulicCircuit 8 | Hydraulic State | 0 | 5 | 0-Error 1-NotActive 2-Off 3-Kick 4-Heating 5-Post_Purge |  | int
INPUT_REGISTER | Read | 7703 |  | i2c | Global Error State | 0 | 4 | 0-No_Error 1-i2c_driver_error 2-Wrong_Cycle_Time 3-Missing_Module_Slot 4-Module_Slot_Error |  | int
INPUT_REGISTER | Read | 7704 |  | i2c | Slot1 Module Detected |  |  | 0-Unknown 1-None 22-FM_CM 25-FM_SI 28-FM_MM 29-FM_MW 30-FM_AM 31-FM_CM2 |  | int
INPUT_REGISTER | Read | 7705 |  | i2c | Slot1 Error State |  |  | 0-No_Error 1-No_Response 2-Wrong_Module 3-Unsupported_Module 4-Internal_Sw_Error 5-Communication_Failed 6-Internal_Module_Error 7-Module_Not_Supported_Current_Variant 8-Module_Not_Suppported_In_Slot 9-Module_Count_Too_High 10-Module_Not_Supported_With_Connected_Boiler_Type |  | int
INPUT_REGISTER | Read | 7706 |  | i2c | Slot2 Module Detected |  |  | 0-Unknown 1-None 22-FM_CM 25-FM_SI 28-FM_MM 29-FM_MW 30-FM_AM 31-FM_CM2 |  | int
INPUT_REGISTER | Read | 7707 |  | i2c | Slot2 Error State |  |  | 0-No_Error 1-No_Response 2-Wrong_Module 3-Unsupported_Module 4-Internal_Sw_Error 5-Communication_Failed 6-Internal_Module_Error 7-Module_Not_Supported_Current_Variant 8-Module_Not_Suppported_In_Slot 9-Module_Count_Too_High 10-Module_Not_Supported_With_Connected_Boiler_Type |  | int
INPUT_REGISTER | Read | 7708 |  | i2c | Slot3 Module Detected |  |  | 0-Unknown 1-None 22-FM_CM 25-FM_SI 28-FM_MM 29-FM_MW 30-FM_AM 31-FM_CM2 |  | int
INPUT_REGISTER | Read | 7709 |  | i2c | Slot3 Error State |  |  | 0-No_Error 1-No_Response 2-Wrong_Module 3-Unsupported_Module 4-Internal_Sw_Error 5-Communication_Failed 6-Internal_Module_Error 7-Module_Not_Supported_Current_Variant 8-Module_Not_Suppported_In_Slot 9-Module_Count_Too_High 10-Module_Not_Supported_With_Connected_Boiler_Type |  | int
INPUT_REGISTER | Read | 7710 |  | i2c | Slot4 Module Detected |  |  | 0-Unknown 1-None 22-FM_CM 25-FM_SI 28-FM_MM 29-FM_MW 30-FM_AM 31-FM_CM2 |  | int
INPUT_REGISTER | Read | 7711 |  | i2c | Slot4 Error State |  |  | 0-No_Error 1-No_Response 2-Wrong_Module 3-Unsupported_Module 4-Internal_Sw_Error 5-Communication_Failed 6-Internal_Module_Error 7-Module_Not_Supported_Current_Variant 8-Module_Not_Suppported_In_Slot 9-Module_Count_Too_High 10-Module_Not_Supported_With_Connected_Boiler_Type |  | int
INPUT_REGISTER | Read | 7712 |  | i2c | Slot A Module Detected |  |  | 0-Unknown 1-None 26-ZM5313 27-ZM5311 |  | int
INPUT_REGISTER | Read | 7713 |  | i2c | Slot A Error State |  |  | 0-No_Error 1-No_Response 2-Wrong_Module 3-Unsupported_Module 4-Internal_Sw_Error 5-Communication_Failed 6-Internal_Module_Error 7-Module_Not_Supported_Current_Variant 8-Module_Not_Suppported_In_Slot 9-Module_Count_Too_High 10-Module_Not_Supported_With_Connected_Boiler_Type |  | int
INPUT_REGISTER | Read | 7714 |  | i2c | irBitblock |  |  |  |  | int
| Read |  | 0 | i2c | Component Error |  |  |  |  | bit
INPUT_REGISTER | Read | 7725 |  | fm-si | irBitblock |  |  |  |  | int
| Read |  | 0 | fm-si | Input 1 Error |  |  |  |  | bit
| Read |  | 1 | fm-si | Input 2 Error |  |  |  |  | bit
| Read |  | 2 | fm-si | Input 3 Error |  |  |  |  | bit
| Read |  | 3 | fm-si | Input 4 Error |  |  |  |  | bit
| Read |  | 4 | fm-si | Input 5 Error |  |  |  |  | bit
INPUT_REGISTER | Read | 7732 |  | Sdc | Demand Mode (Low Priority) | 0 | 2 | 0-Off 1-Take_Heat 2-Give_Heat |  | int
INPUT_REGISTER | Read | 7733 |  | Sdc | Demand Flow Temp (Low Priority) |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7734 |  | Sdc | Demand Mode (High Priority) | 0 | 2 | 0-Off 1-Take_Heat 2-Give_Heat |  | int
INPUT_REGISTER | Read | 7735 |  | Sdc | Demand Flow Temp (High Priority) |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7739 |  | Heat Pump | System return temperature for HP heating buffer |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7740 |  | Heat Pump | Buffer mid temperature for HP heating buffer |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7741 |  | Heat Pump | Buffer top temperature for HP heating buffer |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7742 |  | Heat Pump | Buffer bottom temperature for HP heating buffer |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7743 |  | Heat Pump | Return temperature FWR |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7744 |  | Heat Pump | Flow temperature FWV |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7745 |  | Heat Pump | Flow temperature HP |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7746 |  | Heat Pump | Return temperature HP |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7747 |  | Heat Pump | HMI State of HP Component | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 7748 |  | Heat Pump | HP current heat output |  |  |  | kW | signed int | x10
INPUT_REGISTER | Read | 7749 |  | Heat Pump | HP current electrical power consumption | 0 | 10000 |  | kW | int | x10
INPUT_REGISTER | Read | 7750 |  | Heat Pump | HP Smart grid mode | 0 | 3 | 0-normal_charging_grid 1-low_charging_grid 2-high_charging_grid 3-free_charging_grid |  | int
INPUT_REGISTER | Read | 7751 |  | Heat Pump | Heat demand temperature set point |  |  |  | °C | int
INPUT_REGISTER | Read | 7752 |  | Heat Pump | heatPumpStatusIrBitblock | 0 |  |  |  | int
INPUT_REGISTER | Read | 7753 |  | Heat Pump | Ambient Temperature HP |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7754 |  | Heat Pump | HP silent mode | 0 | 3 | 0-standard_mode 1-silent_mode 2-super_silent_mode 3-night_mode |  | int
INPUT_REGISTER | Read | 7755 |  | Heat Pump | Heat Pump Heat Request Temperature |  |  |  | °C | int
INPUT_REGISTER | Read | 7756 |  | Heat Pump | heatPumpIrBitblock |  |  |  |  | int
INPUT_REGISTER | Read | 7765 |  | System | Open Notifications Count |  |  |  |  | int
INPUT_REGISTER | Read | 7766 |  | System | Error Key 5 |  |  |  |  | long
INPUT_REGISTER | Read | 7768 |  | System | Error Key 6 |  |  |  |  | long
INPUT_REGISTER | Read | 7770 |  | System | Error Key 7 |  |  |  |  | long
INPUT_REGISTER | Read | 7772 |  | System | Error Key 8 |  |  |  |  | long
INPUT_REGISTER | Read | 7774 |  | System | Error Key 9 |  |  |  |  | long
INPUT_REGISTER | Read | 7776 |  | System | Error Key 10 |  |  |  |  | long
INPUT_REGISTER | Read | 7778 |  | Chp / EC Power | Flow Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7779 |  | Chp / EC Power | Return Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7780 |  | Chp | Flue Gas Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7781 |  | Chp | Motor Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7782 |  | Chp / EC Power | Current Generator Power |  |  |  | kW | int
INPUT_REGISTER | Read | 7783 |  | Chp | Current Power Setpoint |  |  |  | kW | int
INPUT_REGISTER | Read | 7784 |  | Chp / EC Power | Operation Hours |  |  |  | h | long
INPUT_REGISTER | Read | 7786 |  | Chp / EC Power | Number of starts |  |  |  |  | long
INPUT_REGISTER | Read | 7788 |  | Chp / EC Power | Hours to Maintenance |  |  |  | h | int
INPUT_REGISTER | Read | 7790 |  | Chp | Output Power Setpoint |  |  |  | kW | int
INPUT_REGISTER | Read | 7791 |  | Chp | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 7796 |  | Chp | irBitblock |  |  |  |  | int
| Read |  | 0 | Chp | Warning |  |  |  |  | bit
| Read |  | 1 | Chp / EC Power | Malfunction |  |  |  |  | bit
| Read |  | 2 | Chp / EC Power | Controlled Shutdown |  |  |  |  | bit
| Read |  | 3 | Chp / EC Power | Generator On |  |  |  |  | bit
| Read |  | 4 | Chp | Automatic On |  |  |  |  | bit
| Read |  | 5 | Chp / EC Power | Automatic Ready |  |  |  |  | bit
| Read |  | 11 | Chp / EC Power | Output On Request |  |  |  |  | bit
INPUT_REGISTER | Read | 7804 |  | Water Treatment Module | Program Step |  |  | 20-140: Desalination not active 10000-10810: One time desalination 20000-20810: Automatic desalination 30000-30260: Stationary operation |  | int
INPUT_REGISTER | Read | 7805 |  | Water Treatment Module | Temperature Desalinization |  |  |  | °C | int | x10
INPUT_REGISTER | Read | 7806 |  | Water Treatment Module | Volume Flow |  |  |  | L/min | int | x10
INPUT_REGISTER | Read | 7807 |  | Water Treatment Module | Conductivity system |  |  |  | uS/cm | int | x10
INPUT_REGISTER | Read | 7808 |  | Water Treatment Module | Conductivity cartridge |  |  |  | uS/cm | int | x10
INPUT_REGISTER | Read | 7809 |  | Water Treatment Module | Cartridge Capacity |  |  |  | % | int
INPUT_REGISTER | Read | 7813 |  | Solar Data | Collector temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7814 |  | Solar Data | Temperature cylinder bottom |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7815 |  | Solar Data | Solar pump modulation setpoint |  |  |  | % | int
INPUT_REGISTER | Read | 7816 |  | Solar | Solar pump status | 0 | 19 | 1-TestMod 2-BlckProt 3-No heat 4-Ht avail 5-SolOff 6-MaxCyl 7-MaxColl 8-MinColl 9-FrostP 10-VacFct 11-SwChck 12-MixPrio 13-Switch 14-Priority 15-ThermD 16-MixCal 17-MixOpn 18-MixCl 19-MixOff |  | int
INPUT_REGISTER | Read | 7817 |  | Solar Data | Heat exchanger temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7818 |  | Solar Data | Heat exchanger pump modulation setpoint |  |  |  | % | int
INPUT_REGISTER | Read | 7819 |  | Solar | Heat exchanger pump status | 0 | 19 | 1-TestMod 2-BlckProt 3-No heat 4-Ht avail 5-SolOff 6-MaxCyl 7-MaxColl 8-MinColl 9-FrostP 10-VacFct 11-SwChck 12-MixPrio 13-Switch 14-Priority 15-ThermD 16-MixCal 17-MixOpn 18-MixCl 19-MixOff |  | int
INPUT_REGISTER | Read | 7820 |  | Solar Data | Temperature cylinder 3 top |  |  |  | °C | int | x10
INPUT_REGISTER | Read | 7821 |  | Solar Data | Reload pump modulation setpoint |  |  |  | % | int
INPUT_REGISTER | Read | 7822 |  | Solar | Reload pump status | 0 | 19 | 1-TestMod 2-BlckProt 3-No heat 4-Ht avail 5-SolOff 6-MaxCyl 7-MaxColl 8-MinColl 9-FrostP 10-VacFct 11-SwChck 12-MixPrio 13-Switch 14-Priority 15-ThermD 16-MixCal 17-MixOpn 18-MixCl 19-MixOff |  | int
INPUT_REGISTER | Read | 7823 |  | Solar | Pump therm. disinfect. status | 0 | 19 | 1-TestMod 2-BlckProt 3-No heat 4-Ht avail 5-SolOff 6-MaxCyl 7-MaxColl 8-MinColl 9-FrostP 10-VacFct 11-SwChck 12-MixPrio 13-Switch 14-Priority 15-ThermD 16-MixCal 17-MixOpn 18-MixCl 19-MixOff |  | int
INPUT_REGISTER | Read | 7824 |  | Solar Yield | Flow temperature heat meter |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7825 |  | Solar Yield | Return temperature heat meter |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7826 |  | Solar Yield | Heat count pulse counter | 0 | 15 |  |  | int
INPUT_REGISTER | Read | 7827 |  | Solar Yield | Solar yield per month |  |  |  | kWh | long | x10
INPUT_REGISTER | Read | 7829 |  | Solar Yield | Solar yield per year |  |  |  | kWh | long | x10
INPUT_REGISTER | Read | 7831 |  | Solar Yield | Last hour solar yield |  |  |  | kWh | long | x10
INPUT_REGISTER | Read | 7833 |  | Solar Yield | Solar yield per day |  |  |  | kWh | long | x10
INPUT_REGISTER | Read | 7835 |  | Solar Yield | Solar yield since installation |  |  |  | kWh | long | x10
INPUT_REGISTER | Read | 7837 |  | Solar | Hmi State | 0 | 6 | 0-Unknown 1-Warning 2-Error 3-Ok 4-Not_Active 5-Critical 6-No_Support |  | int
INPUT_REGISTER | Read | 7838 |  | Solar Data | Hydraulic configuration |  |  |  |  | int
| Read |  | 0 | Solar | Option 1 active |  |  |  |  | bit
| Read |  | 1 | Solar | Option A active |  |  |  |  | bit
| Read |  | 2 | Solar | Option B active |  |  |  |  | bit
| Read |  | 3 | Solar | Option C active |  |  |  |  | bit
| Read |  | 4 | Solar | Option D active |  |  |  |  | bit
| Read |  | 5 | Solar | Option E active |  |  |  |  | bit
| Read |  | 6 | Solar | Option F active |  |  |  |  | bit
| Read |  | 7 | Solar | Option G active |  |  |  |  | bit
| Read |  | 8 | Solar | Option H active |  |  |  |  | bit
| Read |  | 9 | Solar | Option I active |  |  |  |  | bit
| Read |  | 10 | Solar | Option J active |  |  |  |  | bit
| Read |  | 11 | Solar | Option K active |  |  |  |  | bit
| Read |  | 12 | Solar | Option L active |  |  |  |  | bit
| Read |  | 13 | Solar | Option M active |  |  |  |  | bit
| Read |  | 14 | Solar | Option N active |  |  |  |  | bit
| Read |  | 15 | Solar | Option P active |  |  |  |  | bit
INPUT_REGISTER | Read | 7839 |  | Solar Data | irBitblock |  |  |  |  | int
| Read |  | 0 | Solar | Is Active |  |  |  |  | bit
INPUT_REGISTER |  | 7900 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 7901 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 7902 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 7903 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 7904 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 7905 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 7906 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 7907 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 7908 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 7909 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 7910 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 7911 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 7912 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER |  | 7913 |  | Legacy | Reserved for legacy purposes
INPUT_REGISTER | Read | 7922 |  | Energy Monitoring | Heat Output |  |  |  | kW | signed int | x10
INPUT_REGISTER | Read | 7923 |  | Energy Monitoring | Gas Consumption (LCV) |  |  |  | kW | signed int | x10
INPUT_REGISTER | Read | 7925 |  | Energy Monitoring | Electrical Power |  |  |  | W | int
INPUT_REGISTER | Read | 7930 |  | Fresh Water Characteristics 1 | DHW Out Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7931 |  | Fresh Water Characteristics 1 | DHW Volume Flow |  |  |  | L/min | signed int | x10
INPUT_REGISTER | Read | 7932 |  | Fresh Water Characteristics 1 | Prim In Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7933 |  | Fresh Water Characteristics 1 | DHW In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7934 |  | Fresh Water Characteristics 1 | Primary Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 7935 |  | Fresh Water Characteristics 1 | Request DHW Out Temperature |  |  |  | °C | int
INPUT_REGISTER | Read | 7936 |  | Fresh Water Characteristics 1 | Status Request DHW Out Temperature | 0 | 9 | 0-Off 1-DHWRed 2-DHW 3-Sol_red 4-Once_on 5-Therm_d 6-DlyHtUp 7-Preheat_start 8-Preheat_normal 9-No_eq |  | int
INPUT_REGISTER | Read | 7937 |  | Fresh Water Characteristics 2 | Circulation Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 7938 |  | Fresh Water Characteristics 2 | Status Circulation Pump | 0 | 8 | 0-Undefined 1-Test 2-BlckProt 3-No_req 4-AutoOff 5-AutoOn 6-Therm_d 7-Sys_Off 8-DlyHtUp |  | int
INPUT_REGISTER | Read | 7939 |  | Fresh Water Characteristics 2 | Return Valve Modulation Request |  |  |  | % | int
INPUT_REGISTER | Read | 7940 |  | Fresh Water Characteristics 2 | Valve State | 0 | 5 | 0-Undefined 1-TestMod 2-BlckProt 3-Mix_cl 4-Mix_opn 5-Sys_Off |  | int
INPUT_REGISTER | Read | 7941 |  | Fresh Water Characteristics 2 | Return Valve Buffer Temperature |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7942 |  | Fresh Water Characteristics 2 | Disinfection Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 7943 |  | Fresh Water Characteristics 2 | Pump State | 0 | 5 | 0-Undefined 1-TestMod 2-BlckPro 3-No_eq 4-Ht_req 5-Sys_Off |  | int
INPUT_REGISTER | Read | 7944 |  | Fresh Water Characteristics 1 | DHW Valve Power |  |  |  | % | int
INPUT_REGISTER | Read | 7945 |  | Fresh Water Characteristics 2 | Total Flow |  |  |  | L/min | int | x10
INPUT_REGISTER | Read | 7946 |  | Fresh Water 2 | Module 2 DHW Out Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7947 |  | Fresh Water 2 | Module 2 DHW Volume Flow |  |  |  | L/min | signed int | x10
INPUT_REGISTER | Read | 7948 |  | Fresh Water 2 | Module 2 Prim In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7949 |  | Fresh Water 2 | Module 2 DHW In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7950 |  | Fresh Water 2 | Module 2 DHW Valve Power |  |  |  | % | int
INPUT_REGISTER | Read | 7951 |  | Fresh Water 2 | Module 2 Prim Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 7952 |  | Fresh Water 2 | Module 2 Status Prim Pump |  |  |  |  | int
INPUT_REGISTER | Read | 7953 |  | Fresh Water 3 | Module 3 DHW Out Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7954 |  | Fresh Water 3 | Module 3 DHW Volume Flow |  |  |  | L/min | signed int | x10
INPUT_REGISTER | Read | 7955 |  | Fresh Water 3 | Module 3 Prim In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7956 |  | Fresh Water 3 | Module 3 DHW In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7957 |  | Fresh Water 3 | Module 3 DHW Valve Power |  |  |  | % | int
INPUT_REGISTER | Read | 7958 |  | Fresh Water 3 | Module 3 Prim Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 7959 |  | Fresh Water 3 | Module 3 Status Prim Pump |  |  |  |  | int
INPUT_REGISTER | Read | 7960 |  | Fresh Water 4 | Module 4 DHW Out Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7961 |  | Fresh Water 4 | Module 4 DHW Volume Flow |  |  |  | L/min | signed int | x10
INPUT_REGISTER | Read | 7962 |  | Fresh Water 4 | Module 4 Prim In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7963 |  | Fresh Water 4 | Module 4 DHW In Temp |  |  |  | °C | signed int | x10
INPUT_REGISTER | Read | 7964 |  | Fresh Water 4 | Module 4 DHW ValvePower |  |  |  | % | int
INPUT_REGISTER | Read | 7965 |  | Fresh Water 4 | Module 4 Prim Pump Power |  |  |  | % | int
INPUT_REGISTER | Read | 7966 |  | Fresh Water 4 | Module 4 Status Primary Pump |  |  |  |  | int
INPUT_REGISTER | Read | 7967 |  | Fresh Water | Fresh Water Hmi State |  |  |  |  | int
INPUT_REGISTER | Read | 7968 |  | Fresh Water Characteristics 3 | Fresh Water Configurations |  |  |  |  | int
| Read |  | 0 | Fresh Water | Option 2 active |  |  |  |  | bit
| Read |  | 1 | Fresh Water | Option A active |  |  |  |  | bit
| Read |  | 2 | Fresh Water | Option B active |  |  |  |  | bit
| Read |  | 3 | Fresh Water | Option C active |  |  |  |  | bit
| Read |  | 4 | Fresh Water | Option D active |  |  |  |  | bit
| Read |  | 5 | Fresh Water | Option E active |  |  |  |  | bit
| Read |  | 6 | Fresh Water | Option E active cascade module 2 active |  |  |  |  | bit
| Read |  | 7 | Fresh Water | Option E active cascade module 3 active |  |  |  |  | bit
| Read |  | 8 | Fresh Water | Option E active cascade module 4 active |  |  |  |  | bit
| Read |  | 9 | Fresh Water | Is Active |  |  |  |  | bit
INPUT_REGISTER | Read | 7976 |  | System | Error Key 1 |  |  |  |  | long
INPUT_REGISTER | Read | 7978 |  | System | Error Key 2 |  |  |  |  | long
INPUT_REGISTER | Read | 7980 |  | System | Error Key 3 |  |  |  |  | long
INPUT_REGISTER | Read | 7982 |  | System | Error Key 4 |  |  |  |  | long
INPUT_REGISTER | Read | 7984 |  | System | Error 1 Extra Info (MSB) |  |  |  |  | long
INPUT_REGISTER | Read | 7986 |  | System | Error 1 Extra Info (LSB) |  |  |  |  | long
INPUT_REGISTER | Read | 7988 |  | System | Error 2 Extra Info (MSB) |  |  |  |  | long
INPUT_REGISTER | Read | 7990 |  | System | Error 2 Extra Info (LSB) |  |  |  |  | long
INPUT_REGISTER | Read | 7992 |  | System | Error 3 Extra Info (MSB) |  |  |  |  | long
INPUT_REGISTER | Read | 7994 |  | System | Error 3 Extra Info (LSB) |  |  |  |  | long
INPUT_REGISTER | Read | 7996 |  | System | Error 4 Extra Info (MSB) |  |  |  |  | long
INPUT_REGISTER | Read | 7998 |  | System | Error 4 Extra Info (LSB) |  |  |  |  | long